| OGRR Number | 154OGRR | OGRR Title | Generator Protection Requirements |
| --- | --- | --- | --- |
| ###### Date |  | 9/15/04 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Wayne Kemper |  |
| E-mail Address |  | Wayne.kemper@centerpointenergy.com |  |
| Company |  | CenterPoint Energy |  |
| Company Address |  | PO Box 1700 Houston, TX 77251 |  |
| Phone Number |  | 713-207-2192 |  |
| Fax Number |  | 713-207-2444 |  |

Comments

The proposed changes are recommended to ensure that the generator terminal voltage trip points are consistent with TDSP under voltage load shedding set points as well with the over-excitation limits requirements in d(1) of this section (3.1.4.6), ERCOT Security Criteria and manufacturing standards. The ERCOT generating entities need to review the feasibility of this proposal.

Proposed Operating Guide Language Revision

#### 3.1.4.6	Protective Relaying Requirement

The Facility’s generation machine characteristics and plant design shall incorporate the under-frequency firm Load shedding philosophy and criteria defined in Operating Guide 2.9. Requirements for Under-Frequency Relaying.  Inherent in this philosophy is the idea that all generators remain on line until all three steps of firm Load shedding have been executed.  In addition, Generation Resources must remain connected to the transmission system during the following operating conditions:

  - Generator terminal voltages are within seven percent (7%) of the rated nominal design voltage;

  - Generator terminal voltage deviations for the following magnitudes and durations exceeding seven percent (7%).

Terminal Voltage (PU)	.929	.92	.91	.90	.89	.88	.87

Time (seconds)		300	240	180	120	60	30	15

  - Generator volts per hertz conditions are less than one hundred sixteen percent (116%) (of generator nominal voltage) and last for less than 1.5 seconds; and

  - A transmission system fault (three-phase, single-phase or phase-to-phase) is cleared by the primary protection scheme (i.e., no failure of protective devices or transmission breakers) on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in Protocol Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, item (7).

The generation Facility shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria as described in Operating Guide Section 5: Planning.

Within thirty (30) days of ERCOT’s request, Generation Resources shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Generating Resources required to provide VSS shall have and maintain the following capability:

(1)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least eighty percent (80%) of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(2)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment misoperation.