2005

ERCOT Methodologies for Determining Ancillary Service Requirements

Draft – For consideration of the ERCOT board

TABLE OF CONTENTS

Executive Summary	2

Responsive Reserve Service Requirement (RRS)	2

RRS Provision by LAARs	2

Regulation Reserve Requirement	3

Non-Spinning Reserve Requirements	5

Replacement Reserve Requirements	6

Figure - Flow diagram for the RPRS market clearing engine	7

Balancing Energy Requirement	7

Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement	8

# Executive Summary

Protocol 6.4.1(2) requires that ERCOT, at least annually, establish methodologies for determining the minimum quantity requirements for each Ancillary Service needed for reliability . Protocol 6.4.1(4) requires approval of this methodology by the ERCOT Board of Directors.

This document discusses the requirements of the following services:

- Responsive Reserves (RRS),

- Regulation Reserve Service (RGRS),

- Non-Spinning Reserves (NSRS),

- Replacement Reserves, and

- Balancing Energy (including minimum Down Balancing).

For detailed descriptions of these services and their deployment, see Protocol Sections 2 and 6.

Further, detailed methodologies for determining the requirements are attached as part of this document.

# Responsive Reserve Service Requirement (RRS)

Responsive Reserves are resources ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency.  The ERCOT Operating Guides set the RRS requirement at 2300 MW for all hours under normal conditions. The Operating Guides allow ERCOT to increase that requirement under extreme conditions. This quantity will be used until it is determined that a change is appropriate. At that time, the changed methodology will be developed and presented to ERCOT TAC and the ERCOT Board for approval.

### RRS Provision by LAARs

One type of Responsive Reserve is Interruptible Responsive Reserve. Interruptible Responsive Reserve is Load Acting as a Resource (LAAR) that is automatically interrupted when system frequency decreases to 59.7 Hz (or above).

Protocols allow ERCOT to set the percentage of Responsive Reserve that may be served by LAARs. ERCOT calculates the maximum secure RRS that can be provided by LAARS by performing stability analysis of several power flow cases modeling the ERCOT transmission/generation system at different states. ERCOT will examine these models’ response to generator trip events and the response of LAARS/Generation to recover frequency using different generation/LAAR amounts.

The ERCOT Protocols state, “The amount of Resources on high-set under-frequency relays providing RRS will be limited to 50% of the total ERCOT RRS requirement. ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed as prescribed in section 6.4.1, Standards for Determining Ancillary Services Quantities.”

Self arranged Responsive Reserve used to fulfill a QSE’s Responsive Reserve requirement must be at least (100% – maximum LAAR %) % from generation resources. ERCOT procured Responsive Reserve to provide the difference between the 2300 MW system requirement and the amount of Responsive Reserve self arranged by all QSEs must also be at least (100% – maximum LAAR %) % from generation resources.

If the maximum LAAR % level specified in the Protocols is changed, that change will be reflected in these requirements.

# Regulation Reserve Requirement

##### Introduction

Regulation Reserves are resources that can be deployed by ERCOT in response to changes in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.  ERCOT is required to evaluate normal requirements for Regulation Service – Up (regulation up) and Regulation Service – Down (regulation down) on an annual basis. It is ERCOT’s intent to use historical rates of regulation usage to perform this evaluation.

ERCOT proposes that this normal regulation requirement may be increased by a multiple of two (2) during projected severe stress conditions such as forecasted extreme weather days.

##### Summary

To evaluate regulation requirements, ERCOT collects monthly historic deployed regulation data. These data were used to calculate average historically deployed regulation for five-minute periods. By calculating the mean and standard deviation of the amounts of deployed regulation up and deployed regulation down, ERCOT expects it can predict the expected needs for similar months.

By arranging for 2.5 standard deviations times the historic average usage for each hours requirement; ERCOT provides the mathematical expectation that sufficient regulation will be available 98.8% of all periods. This requirement may appear excessive until you realize that this implies that 1.2% of every month, or 35 intervals/month; ERCOT expects to exhaust available regulation services.

##### Procedure

Using archived data, ERCOT will calculate the mean and standard deviation of actual regulation deployed daily for the previous month and the same month of the previous year. Using this data ERCOT will select multiple hour periods of “similar” amounts of reserve deployment, and will, for each of these blocks, select the maximum “average” RRS deployment + 2.5 Standard deviations for the requirement for this block of hours. ERCOT will define between 4 and 6 blocks for each day, and each block may have a different number of hours.  The purpose of the blocks is to facilitate market operations.

ERCOT will calculate and post this requirement by the 20th of each month for each day of the succeeding month as required by the protocols.

If experience indicates that these methods result in repeated shortages of regulation up or regulation down reserves, ERCOT may adjust the regulation requirement to compensate. Before such compensation is applied, ERCOT shall post a message on the Market Information System.  ERCOT shall also provide a report to TAC and the Board of Directors explaining its actions and new methodology at their next meeting.

# Non-Spinning Reserve Requirements

Non-Spinning Reserve Service (NSRS) consists of resources capable of being ramped to a specified output level within thirty (30) minutes or Loads acting as a Resource that are capable of being interrupted within thirty (30).  NSRS is used to replace loss of generating capacity or to compensate for load forecast errors on days in which sufficient spinning reserves are not available.  Spinning reserves are defined as online, unloaded Resource capacity, which is not dedicated for other uses except RRS.

ERCOT will purchase NSRS when the projected risk of insufficiency is higher than normal, such as when hot, cold, or uncertain weather is expected, or when amounts of projected spinning reserves (including RRS) fall below 4,600 MW.

Historically, the need for NSRS has occurred during the following conditions:

	Across peak hours during spring and fall months when hotter than expected weather with large amounts of capacity offline

	Summer seasons when high loads and unit outages outstripped the capability of base load and normal cyclic units.

	Cold weather events when early morning load pickup outpaced the ability of generation to follow.

	Major unit trips when large amounts of spinning reserve were not online.

In each case, the need for quick start non-spinning reserve has been evident when there is not a large excess of spinning reserve on line.

ERCOT believes spinning reserves of 4600 MW (including RRS) is sufficient for normal weather conditions. The April-May and October transition months are not considered “normal” due to a  larger than normal probability of significant load forecast error.

For the purpose of this document, extreme weather days are defined as days in which the forecast peak temperature for ERCOT is projected to be higher than 95 degrees, or the forecast high temperature is lower than 30 degrees, or days in which ERCOT has issued an OCN, Advisory or Alert for adverse weather or an anticipated capacity shortfall.  On extreme weather days, ERCOT will purchase an amount of NSRS equal to the largest unit online for on-peak hours, and may purchase amounts of NSRS greater than this amount in extreme circumstances.

ERCOT will normally use the following in determining the amount of NSRS needed:

1.	Review the weather forecast for the next day and see if it differs significantly from the current day.

2.	If the next day forecast is “similar” to the current day forecast, and the current day forecast high temperature is <95 degrees in Dallas/Ft. Worth or Houston, and the current day low temperature is greater than 30 degrees, and the current day generation plan shows >4600 MW of spinning reserve (including RRS) online all day long, and the current month is not April, May, or October, THEN no NSRS is considered to be required all day for the next day.

3.	Otherwise purchase NSRS using the following:

	If the current month is April, May or October, then purchase NSRS in amounts equal to the largest unit online for the hours projected within 85% of peak hour.

	If today’s and tomorrow’s ERCOT high temperature is projected above 95 degrees in Dallas/Ft. Worth or Houston, then purchase NSRS in amounts equal to the largest unit online for the hours projected warmer than 95 degrees.

	If tomorrow’s low temperature forecast is projected below 30 degrees in Dallas/Ft. Worth or Houston, then purchase NSRS in amounts equal to the largest unit online for the projected morning load pickup hours and hours projected within 85% of peak hour.

	Purchase amounts of NSRS equal to the largest unit online for hours in which the Day Ahead operator estimates spinning reserves online will drop lower than 4600 MW.

# Replacement Reserve Requirements

The purpose of RPRS is to insure the availability of capacity from resources such that the energy from those resources would be available to solve the following system security violations:

- Local congestion

- ERCOT system capacity insufficiency

- Zonal Congestion

The RPRS analysis performs look-ahead analysis of the physical system for each of the hourly time intervals in either the Day Ahead or Adjustment Period Time frame. Based on the study, RPRS procurements are made if the submitted resource plans indicate capacity inadequacy or potential zonal or local congestion for which specific resources are needed to resolve. The procured capacity from these resources must be bid into the Balancing Energy Service market, during the hours for which the RPRS was procured.

The procurement for resolving local congestion is based on a minimal cost approach that uses generic costs for resources and the procurement for capacity insufficiency and zonal congestion.  Hence, the objective of the proposed RPRS market clearing is to minimize the total bid-based cost of procuring the RPRS bids for the whole duration of the Replacement market (i.e. the whole day for Day Ahead Market and the specified time duration for the Adjustment Period) subject to the security constraints not being violated.

If the RPRS analysis software fails to solve correctly, ERCOT staff may OOMC units for security and reliability based upon offline studies.

# Figure - Flow diagram for the RPRS market clearing engine

# Balancing Energy Requirement

Balancing Energy is incremental or decremental energy dispatched by ERCOT by 15-minute Settlement Interval to meet the difference between generation scheduled by the market and ERCOT System load.  Local Balancing Energy Service is also used to resolve local transmission congestion. Balancing Energy is deployed by ERCOT with the goals that (1) Regulation Service in either direction not be depleted during the interval, (2) Regulation Service up and down energy is deployed in each Settlement Interval such that the net energy in regulation is minimized, and (3) to provide for frequency control. ERCOT will estimate Balancing Energy needs based on the actual Load, the difference in forecasted Loads and bilateral schedules, deployed Regulation Service, and forecasted Congestion.

The following three-step approach is used to determine amount and location of BES needed in each Settlement Interval.

Step 1 is to determine balancing energy service needs to resolve generation-load balance and Zonal Congestion.Balancing Energy Service is procured with Local Congestion ignored, i.e., only recognizing Zonal Congestion.

The output of the application will be zonal MCPE, shadow prices of Zonal Congestion and

Portfolio Incremental/Decremental balancing service MW needed by QSE and CM zone.  An estimate will be made of Resource-specific MW outputs (this is intermediate solution and does not indicate resource-specific dispatch instructions).

Step 2 is to determine balancing energy service needs to resolve Local Congestion as well as generation-load balance and Zonal Congestion.

- The transmission security analysis is performed with the MW solutions from Step 1 for checking operational security.

- If no operational constraint violation is detected, the solution from Step 1 is the final solution to the balancing energy service market.

- When any Local Congestion is violated, the solution proceeds as follows:

3.1) The resource-specific incremental premium is taken as the prices for resource-specific incremental bids.

3.2) The resource-specific decremental premium is taken as the prices for resource-specific decremental bids.

3.3) The portfolio balancing service MW solutions by QSE and CM zone obtained in Step 1 are kept as the same at the portfolio level.

3.4) The amount and location of balancing energy service is recalculated with the sum of the incremental and decremental bids cleared due to relief of Local Congestion across all zones to zero. All constraints, including Zonal Congestion and OC, are observed. The objective of Step 2 solution is to minimize the cost of Local Congestion. The output of the application will be as follows:

	Portfolio Incremental/Decremental balancing service MW solutions by QSE and CM zone

	Resource-specific MW outputs (resources that are identified to receive premiums will be sent resource-specific dispatch instructions.)

	Shadow prices of Local Congestion

Step 3 is to determine balancing energy service needs to resolve generation-load balance and Zonal Congestion subject to the local constraint deployments made in step 2.

- Balancing energy service market is cleared with Local Congestion ignored, but with the deployments made in step 2 preserved.

- The market clearing prices from Step 3 will represent the marginal cost for the solution of each constraint and will be produced as an output of the mathematical optimization application. The output of the application will be as follows:

	zonal MCPE

	shadow prices of Zonal Congestion

	Portfolio Incremental/Decremental balancing service MW needed by QSE and CM zone

	Resource-specific MW outputs (this is intermediate solution and does not indicate resource-specific dispatch instructions).

### Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement

For Frequency Control (to correct avoid high frequency)

Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement will be set for all intervals of each day. A down bid percentage requirement will be determined to allow for correcting for high frequency. This is a potential need for all intervals, but is especially needed during minimum load periods.

ERCOT will normally calculate the minimum down balancing requirement for QSE’s as follows.

ERCOT will collect the amount of BES (up and down) deployed and the sum of schedules for each operating period for the two time frames described below:

- The monthly data one year previous to the month to be posted.

- The month to date data on the current month (month previous to the month being analyzed). This interval will generally end on the 19th of the month previous to the month to be posted as the requirements will be posted on the 20th of the preceding month.

From this data ERCOT will calculate the mean balancing energy deployed and a standard deviation.  An amount of down balancing service expected to be sufficient to avoid exhausting the down balancing stack 99.9% of intervals will then be calculated. This amount of down balancing service, expressed as a percentage, will normally be posted as the down balancing percentage requirement. (Note – single outlying historic deployments may be selected in place of this statistical analysis if review indicates such a requirement is justified.)

ERCOT may post this value to be the continuous requirement, or may further analyze the needs to provide a varying requirement by:

- Zone

- On Peak and Off Peak hours

ERCOT may change this requirement during the month if experience shows that the initially proposed requirement is insufficient.

##### For Congestion Management

If a need for additional down balancing is required in a single zone, or zones for congestion management, it is expected by ERCOT that zonal assessment of the data discussed above will allow detection and posting of the need in advance. If this expectation is not correct, ERCOT may adjust the zonal down balancing requirement to address specific congestion events observed.