## Sheet1
TRANSMISSION LOSS FACTORS for 2005 as of 09/17/04
Data from Seasonal SSWG Base Cases Updated with updates received by 9/03/04
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN NOIE INTERNAL TOTAL |  |  |  |  | CPS NOIE INTERNAL TOTAL |  |  |  |  | COG NOIE INTERNAL TOTAL |  |  |  |  | GEUS NOIE INTERNAL TOTAL |  |  |  |  | COD NOIE INTERNAL TOTAL |  |  |  |  | PUB NOIE INTERNAL TOTAL |  |  |  |  | BTU NOIE INTERNAL TOTAL |  |  |  |  | COCS NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 05SPG1 | 59708.8 | 58404.7 | 1206.44 | 1304.17 | 889 | 1890 | 35.87 | 37.6 | 1038.6 | 3116.7 | 3789 | 22.71 | 27.79 | 700.09 | 197.5 | 405.3 | 3.87 | 3.87 | 211.67 | 29.9 | 75.1 | 0.35 | 0.35 | 45.55 | 0 | 264.1 | 1.08 | 1.09 | 265.19 | 63 | 240 | 0.81 | 0.81 | 177.81 | 80 | 168.1 | 2.01 | 2.01 | 90.11 | 0 | 94.9 | 0.15 | 0.15 | 95.05
Spring Off Peak | 05SPG2 | 36469.4 | 35852.9 | 568.22 | 616.47 | 312 | 1045 | 19.88 | 20.33 | 753.33 | 1434.7 | 2124.2 | 8.61 | 10.65 | 700.15 | 33.6 | 135.2 | 0.73 | 0.73 | 102.33 | 8.8 | 31 | 0.06 | 0.06 | 22.26 | 0 | 129.2 | 0.31 | 0.31 | 129.51 | 0 | 170 | 0.61 | 0.61 | 170.61 | 25 | 138.4 | 1.4 | 1.4 | 114.8 | 0 | 73.4 | 0.12 | 0.12 | 73.52
Summer On Peak | 05SUM1 | 70882.1 | 69243.2 | 1517.49 | 1638.83 | 1272 | 2300 | 48.89 | 51.66 | 1079.66 | 3672 | 4334.8 | 30.8 | 37.11 | 699.91 | 309.3 | 514.6 | 6.85 | 6.85 | 212.15 | 60.3 | 105.1 | 0.7 | 0.7 | 45.5 | 0 | 293.4 | 1.04 | 1.03 | 294.43 | 98 | 271 | 0.61 | 0.61 | 173.61 | 150 | 247.2 | 3.74 | 3.73 | 100.93 | 0 | 174.9 | 0.24 | 0.24 | 175.14
Summer Off Peak | 05SUM2 | 42222.2 | 41383 | 786.76 | 839.3 | 237 | 1256.5 | 20.82 | 21.21 | 1040.71 | 1614.8 | 2303.5 | 9.26 | 11.7 | 700.4 | 71.5 | 172.5 | 1.81 | 1.81 | 102.81 | 9.5 | 31.7 | 0.06 | 0.06 | 22.26 | 0 | 149.6 | 0.32 | 0.32 | 149.92 | 67 | 240 | 0.48 | 0.48 | 173.48 | 30 | 128.5 | 1.78 | 1.78 | 100.28 | 0 | 141.2 | 0.16 | 0.16 | 141.36
Fall On Peak | 05FAL1 | 55061.4 | 53852 | 1126.66 | 1209.42 | 980 | 1785 | 35.89 | 37.87 | 842.87 | 3257.9 | 3579 | 23.04 | 28.39 | 349.49 | 172.9 | 380.8 | 3.12 | 3.13 | 211.03 | 45.2 | 90.1 | 0.5 | 0.5 | 45.4 | 0 | 237 | 0.86 | 0.86 | 237.86 | 65 | 237 | 0.45 | 0.45 | 172.45 | 102 | 178 | 2.07 | 2.07 | 78.07 | 0 | 146.6 | 0.15 | 0.15 | 146.75
Fall Off Peak | 05FAL2 | 34264.7 | 33722.1 | 498.16 | 542.6 | 230 | 1055 | 12.28 | 12.63 | 837.63 | 1631.8 | 1971.9 | 7.69 | 9.9 | 350 | 28.5 | 130.1 | 0.88 | 0.88 | 102.48 | 8.8 | 31 | 0.06 | 0.06 | 22.26 | 0 | 120.9 | 0.28 | 0.28 | 121.18 | 62 | 130 | 0.18 | 0.18 | 68.18 | 25 | 123.6 | 1.45 | 1.44 | 100.04 | 0 | 115.5 | 0.14 | 0.14 | 115.64
Winter On Peak | 06WIN1 | 55524 | 54330.4 | 1107.14 | 1193.67 | 941 | 1909 | 38.01 | 39.9 | 1007.9 | 2145.8 | 2823.1 | 19.3 | 22.75 | 700.05 | 185.8 | 393.3 | 3.6 | 3.61 | 211.11 | 25.6 | 70.7 | 0.31 | 0.31 | 45.41 | 0 | 208.3 | 0.97 | 0.98 | 209.28 | 48 | 221 | 0.39 | 0.39 | 173.39 | 142 | 217.5 | 2.4 | 2.41 | 77.91 | 0 | 92.5 | 0.15 | 0.15 | 92.65
Winter Off Peak | 06WIN2 | 39473.8 | 38762.6 | 662.22 | 711.19 | 478 | 1483 | 28.59 | 29.38 | 1034.38 | 1172.8 | 1868.1 | 7.02 | 8.77 | 704.07 | 33.3 | 139.5 | 1.16 | 1.16 | 107.36 | 15.1 | 38.3 | 0.09 | 0.09 | 23.29 | 0 | 82.2 | 0.25 | 0.25 | 82.45 | 87 | 155 | 0.3 | 0.3 | 68.3 | 30 | 136 | 1.37 | 1.37 | 107.37 | 0 | 80.4 | 0.11 | 0.11 | 80.51
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | RE HLP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BEC Self Serve MW | TXU Self Serve MW | AEP DC Tie Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 05SPG1 | 2811.2 | 1175.63 | 553 | 28 | 402 | 0 | 4969.83 |  | 6926.5 | 2624.07 | 4302.43 | 66.85 | 05SPG1
Spring Off Peak | 05SPG2 | 2811.2 | 1175.63 | 553 | 28 | 402 | 0 | 4969.83 |  | 3846.4 | 2066.51 | 1779.89 | 31.72 | 05SPG2
Summer On Peak | 05SUM1 | 2811.2 | 1175.63 | 546.5 | 28 | 402 | 0 | 4963.33 |  | 8241 | 2781.33 | 5459.67 | 92.87 | 05SUM1
Summer Off Peak | 05SUM2 | 2811.2 | 1175.63 | 546.5 | 28 | 402 | 0 | 4963.33 |  | 4423.5 | 2431.22 | 1992.28 | 34.69 | 05SUM2
Fall On Peak | 05FAL1 | 2811.2 | 1175.63 | 546.5 | 28 | 402 | 0 | 4963.33 |  | 6633.5 | 2083.92 | 4549.58 | 66.08 | 05FAL1
Fall Off Peak | 05FAL2 | 2811.2 | 1175.63 | 546.5 | 28 | 402 | 0 | 4963.33 |  | 3678 | 1717.41 | 1960.59 | 22.96 | 05FAL2
Winter On Peak | 06WIN1 | 2811.2 | 1130.34 | 540 | 28 | 402 | 0 | 4911.54 |  | 5935.4 | 2517.7 | 3417.7 | 65.13 | 06WIN1
Winter Off Peak | 06WIN2 | 2811.2 | 1130.34 | 540 | 28 | 402 | 0 | 4911.54 |  | 3982.5 | 2207.73 | 1774.77 | 38.89 | 06WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | PUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 54738.97 | 31499.57 | 2.204% | 1.804% |  | 1890 | 1045 | 1.863% | 1.867% |  | 3789 | 2124.2 | 0.5958% | 0.4037% |  | 405.3 | 135.2 | 0.9458% | 0.537% |  | 75.1 | 31 | 0.4639% | 0.1932% |  | 264.1 | 129.2 | 0.4073% | 0.2394% |  | 240 | 170 | 0.3364% | 0.3575% |  | 168.1 | 138.4 | 1.182% | 1.001% |  | 94.9 | 73.4 | 0.1578% | 0.1632%
SUMMER | 65918.77 | 37258.87 | 2.302% | 2.112% |  | 2300 | 1256.5 | 2.081% | 1.63% |  | 4334.8 | 2303.5 | 0.7055% | 0.4004% |  | 514.6 | 172.5 | 1.314% | 1.038% |  | 105.1 | 31.7 | 0.6616% | 0.1889% |  | 293.4 | 149.6 | 0.3532% | 0.2134% |  | 271 | 240 | 0.2246% | 0.1996% |  | 247.2 | 128.5 | 1.49% | 1.366% |  | 174.9 | 141.2 | 0.137% | 0.1132%
FALL | 50098.07 | 29301.37 | 2.249% | 1.7% |  | 1785 | 1055 | 1.971% | 1.151% |  | 3579 | 1971.9 | 0.6396% | 0.3885% |  | 380.8 | 130.1 | 0.8127% | 0.6719% |  | 90.1 | 31 | 0.5519% | 0.1932% |  | 237 | 120.9 | 0.3616% | 0.2311% |  | 237 | 130 | 0.1895% | 0.1383% |  | 178 | 123.6 | 1.15% | 1.16% |  | 146.6 | 115.5 | 0.1022% | 0.1211%
WINTER | 50612.46 | 34562.26 | 2.187% | 1.916% |  | 1909 | 1483 | 1.952% | 1.891% |  | 2823.1 | 1868.1 | 0.679% | 0.3744% |  | 393.3 | 139.5 | 0.907% | 0.8247% |  | 70.7 | 38.3 | 0.4366% | 0.2344% |  | 208.3 | 82.2 | 0.4635% | 0.3032% |  | 221 | 155 | 0.1762% | 0.1932% |  | 217.5 | 136 | 1.091% | 0.9973% |  | 92.5 | 80.4 | 0.1619% | 0.1366%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  | For Testing Only |  |  | AEN NOIE INTERNAL |  | For Testing Only |  |  | CPS NOIE INTERNAL |  | For Testing Only |  |  | COG NOIE INTERNAL |  | For Testing Only |  |  | GEUS NOIE INTERNAL |  | For Testing Only |  |  | COD NOIE INTERNAL |  | For Testing Only |  |  | PUB NOIE INTERNAL |  | For Testing Only |  |  | BTU NOIE INTERNAL |  | For Testing Only |  |  | COCS NOIE INTERNAL |  | For Testing Only
| SSC | SIC | 42555.9 |  |  | SSC | SIC | 2022.1 |  |  | SSC | SIC | 2920.1 |  |  | SSC | SIC | 381.1 |  |  | SSC | SIC | 77.1 |  |  | SSC | SIC | 252 |  |  | SSC | SIC | 204 |  |  | SSC | SIC | 279 |  |  | SSC | SIC | 108
SPRING | 1.7216e-05 | 1.2616 | 1.9942 |  |  | -5.1387e-06 | 1.8722 | 1.8619 |  |  | 0.00011539 | 0.15858 | 0.49553 |  |  | 0.0015134 | 0.33243 | 0.90919 |  |  | 0.0061385 | 0.0028803 | 0.47616 |  |  | 0.0012447 | 0.078552 | 0.39221 |  |  | -0.00030251 | 0.40897 | 0.34726 |  |  | 0.0060659 | 0.16191 | 1.8543 |  |  | -0.00025159 | 0.18169 | 0.15452
SUMMER | 6.6454e-06 | 1.864 | 2.1468 |  |  | 0.00043261 | 1.0864 | 1.9612 |  |  | 0.00015021 | 0.054371 | 0.49301 |  |  | 0.00080463 | 0.89958 | 1.2062 |  |  | 0.0064402 | -0.015237 | 0.4813 |  |  | 0.00097195 | 0.068044 | 0.31297 |  |  | 0.000806 | 0.0061614 | 0.17058 |  |  | 0.0010456 | 1.2319 | 1.5236 |  |  | 0.00070763 | 0.013269 | 0.089693
FALL | 2.6388e-05 | 0.92692 | 2.0499 |  |  | 0.0011239 | -0.035095 | 2.2375 |  |  | 0.00015629 | 0.080277 | 0.53666 |  |  | 0.00056167 | 0.59878 | 0.81284 |  |  | 0.0060694 | 0.0050229 | 0.47297 |  |  | 0.001124 | 0.09517 | 0.37842 |  |  | 0.00047891 | 0.076012 | 0.17371 |  |  | -0.00018352 | 1.1822 | 1.131 |  |  | -0.00060613 | 0.19107 | 0.12561
WINTER | 1.6913e-05 | 1.3315 | 2.0512 |  |  | 0.00014281 | 1.6796 | 1.9684 |  |  | 0.00031898 | -0.22151 | 0.70994 |  |  | 0.00032445 | 0.77942 | 0.90307 |  |  | 0.0062383 | -0.0044923 | 0.47648 |  |  | 0.0012712 | 0.19872 | 0.51907 |  |  | -0.0002578 | 0.23313 | 0.18054 |  |  | 0.0011546 | 0.84028 | 1.1624 |  |  | 0.0020885 | -0.031285 | 0.19427