## ERCOT Operations Report

## ROS & OWG

## September 2004

August Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 9/9/2004 0:02 | 60.102 | 29178 | -59 | 478 | -3000 (-650) |
| 9/9/2004 9:22 | 60.107 | 32349 | 64 | -998 | 09:18 failover (RRS Deployed) |
| 9/9/2004 10:06 | 60.102 | 34244 | -391 | -1054 | 1425 (640) |
| 9/10/2004 0:19 | 59.899 | 29539 | 566 | 100 | -1950 (-460) |
| 9/14/2004 1:59 | 60.107 | 31472 | -21 | 704 | -1575 (-300) |
| 9/16/2004 6:06 | 59.899 | 33429 | -116 | -287 | 3000 (660) |
| 9/17/2004 0:05 | 60.119 | 36294 | -446 | 579 | -1600 (-870) |
| 9/21/2004 17:21 | 60.114 | 47769 | -800 | -542 | Overshoot from unit trip |
| 9/23/2004 1:07 | 60.106 | 29839 | -348 | 413 | -1000 (-370) |
| 9/24/2004 0:01 | 60.114 | 32450 | -72 | 729 | -3150 (-690) |
| 9/25/2004 6:00 | 60.104 | 27576 | -269 | 817 | 100 (400) |
| 9/26/2004 23:59 | 60.103 | 29725 | -123 | 432 | -985 (-365) |
| 9/27/2004 0:00 | 60.111 | 29637 | -262 | 449 | -2050 (-620) |
| 9/27/2004 5:34 | 60.103 | 27440 | -522 | 426 |  |

Disturbances

|  | Sept Trips | MW Lost |
| --- | --- | --- |
| 9/1/2004 16:49 | 59.896 | 420 |
| 9/2/2004 8:40 | 59.882 | 550 |
| 9/12/2004 10:09 | 59.881 | 420 (2 Units) |
| 9/21/2004 16:44 | 59.872 | 550 |
| 9/28/2004 19:12 | 59.898 | 280 (2 Units) |

Deployed Responsive  (35) (Reported Above)

| 9/1/04 16:49 | 9/9/04 6:06 | 9/16/04 17:01 | 9/24/04 11:25 | 9/28/04 6:04 |
| --- | --- | --- | --- | --- |
| 9/1/04 22:03 | 9/9/04 9:18 ** | 9/17/04 0:34 | 9/25/04 6:08 | 9/28/04 10:01 |
| 9/1/04 23:30 | 9/10/04 0:19 | 9/17/04 15:18 | 9/25/04 22:04 | 9/28/04 19:12 |
| 9/2/04 6:08 | 9/10/04 12:03 | 9/18/04 5:04 | 9/27/04 6:02 | 9/29/04 18:11 |
| 9/2/04 8:40 | 9/12/04 0:29 | 9/21/04 16:44 | 9/27/04 10:53 | 9/30/04 6:08 |
| 9/6/04 6:06 | 9/12/04 10:09 | 9/22/04 15:40 | 9/27/04 20:28 | 9/30/04 8:58 |
| 9/7/04 6:03 | 9/16/04 6:06 | 9/23/04 6:07 | 9/27/04 22:10 | 9/30/04 22:03 |

** Responsive deployed when POS failover defaulted frequency to 58.5 Hz.

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Sept '03 | Aug '04 | Sept '04 |
| --- | --- | --- | --- |
| DFW | 218 | 305 | 88 |
| E RIO | 85 | 107 | 74 |
| W RIO | 46 | 54 | 56 |
| Laredo | 77 | 93 | 81 |
| Bryan Area | 0 | 18 | 23 |
| Corpus | 29 | 31 | 30 |
| Abilene | 58 | 31 | 30 |
| San Angelo | 56 | 29 | 30 |
| Western | 29 | 0 | 0 |
| Houston | 5 | 0 | 0 |
| San Antonio | 1 | 0 | 2 |
|  | 604 | 686 | 418 |

OOME / Congestion Management Activity

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Heights Sub - Freeway Park | Heights - PH Robinson | 22 |
| Gibbons Creek - Greens Prarie/East | TAMU - Dansby | 20 |
| Uvalde - Hamilton | Asherton - West Conoco | 18 |
| N McCallen - N Edinburg | Polk - Hall Acres | 16 |
| Austrop - Sandow | Austrop Tr | 12 |
| N Edinburg - Bates | McColl Rd - McCallen | 12 |
| Gibbons Creek - Greens Prarie/East | Hearne - Hearne Cty | 11 |
| South - Houston CSC |  | 11 |
| Gibbons Creek - Greens Prarie/East | Briarcrest - Nall Lane | 10 |
| South - North CSC |  | 10 |
| Big Brown - Richland Chambers | Trinidad TR 6H | 8 |
| Morgan Creek - Eskota | Eskota Tr | 8 |
| West Levee - Sargent Rd | Cedar Hill - Watermill | 8 |
| West Yates - N McCamey | Ft Lancaster - Illinois | 8 |
| La Palma - Rio Hondo | La Palma - Rio Hondo | 7 |
| N Edinburg - Rio Hondo | S McCallen - Las Milpas | 6 |
| Calaveras- Skyline/Walzem Rd | Calaveras - Ball Park | 5 |
| N Edinburg - Rio Hondo | Hiedelberg - Weslaco | 5 |
| Citgo Oak Park - Highway 9 | Nueces Bay - Hiway 9 | 4 |
| Clear Springs - Marion/Zorn | Seguin - Seguin West | 4 |
| Gibbons Creek - Twin Oaks Switch | Jewet - Watsons Chapel | 4 |
| Asherton - Eagle Pass | Uvalde - Asphalt Mines | 3 |
| Clear Springs - Marion/Zorn | SMI - McQueeney | 3 |
| Frontera - S McCallen | N McCallen - W McCallen | 3 |
| Morgan Creek - Odessa | Odessa - Big Three | 3 |
| N Denton - W Denton | N Sanger - Spring | 3 |
| Allen Renner/Tennyson | Allen Plano Alma Rd | 2 |
| Asherton - W Conoco |  | 2 |
| Big Lake - N McCamey | Fort Lancaster - Illinois 4 | 2 |
| Gibbons Creek - Greens Prarie/East | Atkins - Briarcrest | 2 |
| Live Oak - Sonora | El Dorado - Live Oak | 2 |
| Northeast - North CSC |  | 2 |
| Rio Hondo Tr | Rio Hondo - La Palma | 2 |
| Sandow Tr. | Robertson - Milano | 2 |
| Sandow Tr. |  | 2 |
| Sargent - Watermill | Cedar Hill - Watermill | 2 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Allen Switch - Royse Switch/Monticello | Centerville Sw - Garland Rd | 1 |
| Benbrook -Parker/Graham | Stephenville - Lingleville | 1 |
| Burnet - Wirtz | Ferguson - Sherwood Shores | 1 |
| Cedar Bayou Tr 3 | Cedar Bayou - Baytown | 1 |
| Clear Springs - Marion/Zorn | Cico - Comfort | 1 |
| Clear Springs - Marion/Zorn | Comal - Loop 337 | 1 |
| Clear Springs - Marion/Zorn | Asherton - W Conoco | 1 |
| Collin - Anna Sw | Whtesboro Jordan Tr | 1 |
| Comanche Peak - Parker Sw | Wolf Hollow - Rocky Creek | 1 |
| Crane - Rio Pecos | Ft Lancaster - Illinois | 1 |
| Elgin Sw - Taylor |  | 1 |
| Fort Stockton Tr | Rio Pecos Tr | 1 |
| Frontera - S McCallen | Bates Tr | 1 |
| Hamilton Road - Sonora | Asherton - West Conoco | 1 |
| Heights Sub - Freeway Park | GAF Sub - PH Robinson | 1 |
| Marion - Hill Country/Skyline | Schertz - Parkway | 1 |
| Mesquite E - Mesquite W | Duck Creek Tap - Forney Switch | 1 |
| Midland East - Odessa | Odessa - Odessa North | 1 |
| Morgan Creek - Eskota | Merkel - Scott | 1 |
| Monticello Tr |  | 1 |
| N Edinburg - Rio Hondo | N Edinburg - McColl Rd | 1 |
| N Edinburg - Rio Hondo | Pharr - Pharr MVEC | 1 |
| N Edinburg - Rio Hondo | Weslaco - N Weslaco | 1 |
| N McCallen - N Edinburg | Polk - Pharr | 1 |
| North - Houston CSC |  | 1 |
| Odessa T2 | Odessa T1 | 1 |
| Oklaunion - Fisher Road/ Bowman | Vernon - Grayback | 1 |
| Roanoke - Parker | Benbrook - Calmont | 1 |
| Sandow Tr. | Gilland Creek - Elgin | 1 |
| Spunky - Hood |  | 1 |
| STP - Dow | Blessing - Lane City | 1 |
| Temple Sw - Killeen/Sandow | Belton - Nolanville | 1 |
| Trinidad - Richland Chambers | Venus - Webb | 1 |
| Uvalde - Hamilton | West Conoco - Pueblo | 1 |
| Valley Tr 1 |  | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

Generation dispatch at STP to protect STP – WA Parrish upon the loss of the double STP – DOW lines.

# Security Alert Stage/ Threatcon/ Related issues

None

Major system voltage problems

None

New Procedures/ Forms/ Operations Bulletins

| 09/30/2004 | ERCOT Power Operations Bulletin 113 | Temporary Change - Frequency Control Desk CN#160 |
| --- | --- | --- |
| 09/30/2004 | ERCOT Power Operations Bulletin 112 | Temporary Change - Operating Period Desk CN#159 |
| 09/30/2004 | ERCOT Power Operations Bulletin 111 | Temporary Change - Frequency Control Desk CN#158 |
| 09/27/2004 | ERCOT Power Operations Bulletin 110 | Phase II Implementation of PRR 425 |
| 09/20/2004 | ERCOT Market Operations Bulletin 19 | The Relationship between Resource-specific Instructed Deviations and Portfolio Balancing Energy Bids |

Blackout/Load Shed incidences

9/1	17:00 – 19:00 	75 MW Laar interrupted for transmission security.

9/3	04:30-06:30 Multiple 138 kV lines tripped in Galveston County and approximately 24 MW load was

lost.  Static line failure was the reported cause.

# Communication

9/10 	10:30 – 11:30   Portal Down

9/14	Held 10:45 interval

9/14	Held 14:00 interval

9/23	Portal down 05:45 – 6:20.

9/25	13:00 – 14:30	A/S Market extended

ERCOT peak (Unofficial)

9/17	56,000

OCN, Advisory, Alert, Emergency Notice and Major Events

9/9  13:40-18:00  OCN issued.  Load forecast exceeded projected capacity

9/10 08:00 -21:00  OCN issued.  Load forecast exceeded projected capacity

9/10 10:30 -11:30  Alert issued.  Load forecast exceeded projected capacity

9/15 15:00 – 18:15  Alert issued.  Insufficient Up Balancing in North, South, and Houston Zones.

9/16 14:00 – 24:00  Alert issued.  Insufficient Up Balancing in North, Northeast, and West Zones.

9/17 15:00 – 18:00  OCN issued.  Insufficient Up Balancing projected.

9/17 16:00 – 18:00  OCN issued.  Insufficient capacity projected.

|  | Robertson - Milano | Sandow Tr | Dilley - San Miguel loads Derby - Pearsall | Rio Hondo - La Palma loads Rio Hondo - La Palma | Uvalde - Hamilton loads Asherton - West Conoco | Uvalde - Asphalt Mines | Midland E - Odessa loads Odessa - Odessa North | Live Oak - Sonora laods El Dorado - Live Oak | Gibbons Creek - Bryan East/Greens Prarie loads Dansby - TAM | Gibbons Creek - Bryan East/Greens Prarie loads BriarCrest - Nall Lane | N Edinburg - Bates loads N McCallen - McColl Rd | N Denton - West Denton loads N Sanger - Spring | Aransas Pass - Ingleside loads Rincon - Rockport | (Contingency loads Element) | Transmission Alerts |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9/1 | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/2 | * |  |  |  | * |  |  |  |  |  |  |  |  |  |  |
| 9/3 | * | * |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/5 |  |  | * |  |  |  |  |  |  |  |  |  | * |  |  |
| 9/6 |  |  | * | * |  |  |  |  | * | * | * |  | * |  |  |
| 9/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/9 |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |
| 9/10 |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |
| 9/11 |  |  |  |  | * | * |  |  |  |  |  |  |  |  |  |
| 9/12 |  |  |  |  | * | * |  |  | * |  |  |  |  |  |  |
| 9/13 |  |  |  |  | * | * |  |  | * | * |  |  |  |  |  |
| 9/14 |  |  | * |  | * | * |  |  | * |  |  |  |  |  |  |
| 9/15 |  |  |  |  | * | * |  |  | * |  |  |  |  |  |  |
| 9/16 |  |  |  |  | * |  |  |  | * |  |  |  |  |  |  |
| 9/17 |  |  |  |  |  |  | * |  | * | * |  |  |  |  |  |
| 9/18 |  |  |  |  | * |  |  |  | * | * |  | * |  |  |  |
| 9/19 |  |  |  |  |  |  |  |  | * | * |  |  |  |  |  |
| 9/20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/21 |  |  |  |  |  |  |  |  | * | * |  |  |  |  |  |
| 9/22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/23 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/24 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9/26 |  |  |  |  |  |  |  |  |  |  |  | * |  |  |  |
| 9/27 |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |
| 9/28 |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |
| 9/29 |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |
| 9/30 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |