| PRR Number | 535PRR | PRR Title | Reactive Testing |
| --- | --- | --- | --- |
| Recommended Action |  | Approve |  |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.10.3.5, Reactive Supply from Generation Resources Required to Provide VSS |  |
| Proposed Effective Date |  | November 1, 2004 |  |
| Priority & Rank Assigned |  | Not Applicable |  |
| Revision Description |  | The changes consist of revising the wording to reflect capability vs. capacity during testing, more clearly specifying that reactive testing is at a minimum every two years vs. “interval no more often than once every two years” and specifying the MW level that a generator is to be tested. |  |
| Benefit |  | This PRR is to clarify this section and to minimize the possibility of misinterpretation of the time period between testing of a generator’s reactive capability. |  |
| PRS Recommendation |  | PRS recommends approval of PRR535 as revised by PRS. |  |

| Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen for the Generator Reactive Testing Procedures Task Force |
| E-mail Address | jack.thormahlen@lcra.org |
| Company | LCRA |
| Company Address | P.O. Box 220, Austin, Texas 78767 |
| Phone Number | 512-473-3200 ext 2635 |
| Fax Number | 512-469-6856 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | none | none | Testing Periods would reflect intent of biennial testing form |
| MARKET SEGMENT | none | none | none |
| Consumer | none | none | none |
| LSE: General, Including NOIE | none | none | none |
| LSE: CR & REP | none | none | none |
| QSE | QSE will be able to plan for the biennial testing more efficiently | none | QSE will be able to coordinated the testing more efficiently |
| Resource | Generators will be able to plan a more specific testing program | none | Generators will have a more specified period between testing intervals. |
| TDSP | TDSP will be able to plan for the biennial testing more efficiently | none | TDSP will be able to coordinated the testing more efficiently |

Proposed Protocol Language Revision

6.10.3.5	Reactive Supply from Generation Resources required to provide VSS

- The Generation Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources required to provide VSS, as required by the Operating Guides.  Generation Resources required to provide VSS reactive capability limits shall be specified considering nominal substation voltage.

- The Generation Entity will conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests will be performed on initial qualification and at a minimum of once every two years.  ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Generation Entity is not obligated to place Generation Resources required to provide VSS On-line solely for testing.  The reactive capability tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

- Maximum lagging power factor reactive operating limit shall be demonstrated during peak Load Season, at or above 95% of the most currently tested net dependable megawatt capability, insofar as system voltage conditions and other factors will allow.  The Generation Resource required to provide VSS should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

- Maximum leading power factor reactive operating limit shall be demonstrated during light Load conditions, with the unit operating at a typical output for that condition, insofar as system voltage conditions and other factors will allow.  The unit should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

- The Generation Entity shall perform the unit Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every five (5) years.  The AVR tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
|  | None submitted |

| Sponsor's Revision Description | The changes consist of revising the wording to reflect capability vs. capacity during testing, more clearly specifying that reactive testing is at a minimum every two years vs. “interval no more often than once every two years” and specifying the MW level that a generator is to be tested. |
| --- | --- |
| Sponsor's Reason for Revision | This PRR is to clarify this section and to minimize the possibility of misinterpretation of the time period between testing of a generator’s reactive capability. |