| OGRR Number | 154OGRR | OGRR Title | Generator Protection Requirements |
| --- | --- | --- | --- |
| ###### Date |  | 10-18-2004 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Glenn Hargrave |  |
| E-mail Address |  | grhargrave@cps-satx.com |  |
| Company |  | City Public Service |  |
| Company Address |  | 145 Navarro San Antonio, TX 78205 |  |
| Phone Number |  | (210) 353-4215 |  |
| Fax Number |  | (210) 353-4449 |  |

Comments

CPS comments to AEP Comments 100404 are listed below each bullet.

Revised Proposed Operating Guide Language

#### 3.1.4.6	Protective Relaying Requirement

The Facility’s generation machine characteristics and plant design shall incorporate the under-frequency firm Load shedding philosophy and criteria defined in Operating Guide 2.9. Requirements for Under-Frequency Relaying.  Inherent in this philosophy is the idea that all generators remain on line until all three steps of firm Load shedding have been executed.  In addition, Generation Resources must remain connected to the transmission system during the following operating conditions:

  - Generator terminal voltages are within seven percent (7%) of the rated nominal design voltage;

- Comment:  For overvoltage, I am not sure that the value should be raised from 5% to 7% for continuous operation.  I think that generator standards require that generators only be capable of operating continuously up to 1.05 pu of rating.  However, ten seconds for 105% to 110% may be too fast and a time in minutes should be considered.  For undervoltage protection, I do agree that it should coordinate with undervoltage load shedding.  Additionally, undervoltage relaying is not a typical or recommended type of protection for a generator, so I am not sure what type of damage undervoltage can do to a generator.

  - Generator terminal voltage deviations for the following magnitudes and durations exceeding seven percent (7%).

Terminal Voltage (PU)	.929	.92	.91	.90	.89	.88	.84	.8

Time (seconds)	300	240	180	120	60	30	15	2

  - Generator volts per hertz conditions are less than one hundred sixteen percent (116%) (of generator nominal voltage) and last for less than 1.5 seconds; and

- Comment:  This is acceptable as well and falls within typical settings of recommended volts per hertz protection.  However, I think that maybe it should add a lower limit of 105% for tripping.  I think that generator standards allow continuous operation of to 105% volts per hertz, so maybe there should be a statement regarding staying connected when volts per hertz is less than 105%.

  - A transmission system fault (three-phase, single-phase or phase-to-phase) is cleared by the primary protection scheme (i.e., no failure of protective devices or transmission breakers) on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in Protocol Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, item (7).

- Comment: The only comment that I have to here regards situations where tripping the transmission line islands the generator switchyard.  In particular, I am considering a station where we only have two lines out of the station.  If we only have one line in service and that line faults, the generators may be tripped offline due to load rejection.  Also, the two lines out of this station share common towers, so simultaneous faults on both lines is possible and would possibly trip the generators offline due to load rejection as well.  I don’t think that the requirements written above are intending for the generator to stay connected to the transmission system during this type of contingency, it just isn’t spelled out.

The generation Facility shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria as described in Operating Guide Section 5: Planning.

Within thirty (30) days of ERCOT’s request, Generation Resources shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Generating Resources required to provide VSS shall have and maintain the following capability:

(1)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least eighty percent (80%) of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(2)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment misoperation.