## ERCOT Operations Report

## ROS & OWG

## August 2004

August Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 8/15/2004 21:55 | 60.112 | 37980 | -993 | 979 | -3490 (-1215) |
| 8/16/2004 6:51 | 60.105 | 30910 | -858 | 349 |  |
| 8/19/2004 13:09 | 60.101 | 44361 | -740 | -147 | Out of Down Reg 13:05 - 13:30. Frequency above 60.05 for 10 minutes. VDI's issued to reduce generation. |
| 8/24/2004 6:51 | 60.132 | 37409 | -797 | -162 | Offset entered (+) vise (-). VDI's issued to counterbalance offset |
| 8/28/2004 5:55 | 60.130 | 31704 | -381 | 455 |  |

Disturbances

|  | August Trips | MW Lost |
| --- | --- | --- |
| 8/5/2004 12:38 | 59.897 | 400 MW |
| 8/7/2004 13:05 | 59.801 | 820 MW |
| 8/11/2004 8:48 | 59.872 | 540 MW |
| 8/12/2004 7:59 | 59.899 | 370 MW |
| 8/18/2004 10:01 | 59.772 | 1420 MW (2 stations/ 9 Units) |
| 8/19/2004 11:08 | 59.748 | 1230 MW (1 station/ 8 Units) |
| 8/19/2004 18:16 | 59.847 | 700 MW (1 Station/3 Units) |
| 8/25/2004 14:33 | 59.858 | 650 MW (1 Station/3 Units) |
| 8/27/2004 10:45 | 59.866 | 445 MW (1 station/ 3 Units) |

Deployed Responsive   (27)

| 8/3/04 1:10 | 8/16/04 22:04 | 8/24/04 6:05 |
| --- | --- | --- |
| 8/5/04 12:38 | 8/17/04 22:03 | 8/24/04 8:04 |
| 8/7/04 13:05 | 8/18/04 9:59 | 8/25/04 14:33 |
| 8/8/04 9:01 | 8/18/04 10:25 | 8/26/04 20:01 |
| 8/11/04 8:48 | 8/19/04 6:03 | 8/27/04 10:45 |
| 8/12/04 7:59 | 8/19/04 8:05 | 8/27/04 19:02 |
| 8/14/04 0:04 | 8/19/04 11:08 | 8/28/04 22:03 |
| 8/14/04 10:06 | 8/19/04 18:15 | 8/31/04 22:05 |
| 8/15/04 21:59 | 8/23/04 22:00 | 8/31/04 22:45 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Aug '03 | July '04 | Aug '04 |
| --- | --- | --- | --- |
| DFW | 411 | 324 | 305 |
| E RIO | 119 | 108 | 107 |
| W RIO | 34 | 59 | 54 |
| Laredo | 89 | 91 | 93 |
| Brazos Area | 0 | 0 | 18 |
| Corpus | 30 | 31 | 31 |
| Abilene | 37 | 31 | 31 |
| San Angelo | 30 | 31 | 29 |
| Western | 28 | 6 | 0 |
| Houston | 1 | 2 | 0 |
| San Antonio | 1 | 0 | 0 |
|  | 786 | 686 | 672 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Austrop - Sandow | Austrop Tr | 20 |
| Gibbons Creek - Twin Oaks Switch | Jewet - Watsons Chapel | 16 |
| Marion - Hill Country/Skyline | Cibolo - Schertz | 14 |
| Gibbons Creek - Greens Prarie/East | Hearne - Hearne Cty | 13 |
| N McCallen - N Edinburg | Polk - Hall Acres | 13 |
| South - Houston CSC |  | 12 |
| Gibbons Creek - Greens Praire/East | Briarcrest – Nall Lane | 11 |
| West Yates - N McCamey | Ft Lancaster - Illinois | 11 |
| N Denton - W Denton | N Sanger - Spring | 10 |
| Gibbons Creek - Greens Prarie/East | TAMU - Dansby | 8 |
| N Edinburg - Bates | McColl Rd - McCallen | 7 |
| N Edinburg - Rio Hondo | S McCallen - Las Milpas | 7 |
| Rio Hondo - La Palma | Rio Hondo - La Palma | 6 |
| Uvalde - Hamilton | Asherton - West Conoco | 6 |
| North - Houston CSC |  | 5 |
| Hamilton Road - Sonora | Asherton - West Conoco | 4 |
| Midland East - Odessa | Odessa - Odessa North | 4 |
| Odessa Switch - Moss | Moss Sw - Amaco N Cowden Tap | 4 |
| SA Red Creek Tr 2 | SA Red Creek Tr 1 | 4 |
| Aransas Pass - Ingleside | Rincon - Rockport | 3 |
| Big Brown - Jewett | Tricorner - Watermill | 3 |
| Big Lake - N McCamey | Fort Lancaster - Illinois 4 | 3 |
| Gibbons Creek - East | Gibbons Creek - Greens Prarie | 3 |
| Lake Whitney - Olson | Kileen Sw - Kileen Ft Hood | 3 |
| Mt Enterprise - Trinidad / Martin Lake - Stryker Creek | Nacogdoches - Nacogdoches S | 3 |
| N McCamey - Rio Pecos | McCamey - Rankin | 3 |
| Temple - Lake Creek/Tradinghouse | Lake Creek - Temple | 3 |
| Abeline Mulberry W1 Tr | Abeline Mulberry W1 Tr | 2 |
| Benbrook Sw - Calmont | Hanley - Randol Mill East Tap | 2 |
| Buda - Turnerville | Marshall Ford - Hicross | 2 |
| Citgo Oak Park - Highway 9 | Nueces Bay - Hiway 9 | 2 |
| Clear Springs - Marion/Zorn | Seguin - Seguin West | 2 |
| Industrial - Denton Arco | N Denton T1 | 2 |
| La Palma - Rio Hondo |  | 2 |
| Lon Hill Tr 2 | Lon Hill Tr 1 | 2 |
|  | N Denton T1 | 2 |
| N Edinburg - Rio Hondo | Weslaco - N Weslaco | 2 |
| N McCallen - N Edinburg | Pharr - Pharr MVEC | 2 |
| Northeast - North CSC |  | 2 |
| Odessa T2 | Odessa T1 | 2 |
| South - North CSC |  | 2 |
| STP - Dow | Blessing - Lane City | 2 |
| STP - Skyline/Hill Country | Blessing - Lolita | 2 |
| Vernon - Lake Pauline | Vernon - Chillicothe | 2 |
| West Levee - Sargent Rd | Cedar Hill - Watermill | 2 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Bates - Frontera | McCallen - McColl Rd | 1 |
| Benbrook -Parker | Wedgewood - Bryant Irving | 1 |
| Big Brown - Richland Chambers | Tricorner - Watermill | 1 |
| Big Brown - Venus Switch | Watermill - Cedar Hill Switch | 1 |
| Bowman Switch - Graham | Wichita Falls - Fisher Road | 1 |
| East Tr 138/69 kV | Iola - Keith | 1 |
| Frontera - S McCallen | Bates Tr | 1 |
|  | Hamilton Road - Sonora | 1 |
| Jefferson - Crown | Jefferson - Collage | 1 |
| Lake Creek - Jewett | Navarro - Richland Chambers | 1 |
| Lake Whitney - Olson | Lake Whitney - Olson | 1 |
| Live Oak - Sonora | El Dorado | 1 |
| Marion - Hill Country/Zorn | Marion Tr 2 | 1 |
| Marion - Hill Country/Zorn | GPI - Loop 337 | 1 |
| Maritin Lake - Elkton/Tricorner | Stryker Creek - Summerfield | 1 |
| Midland East - Odessa | Midland West - Odessa | 1 |
| Midland East - Odessa | Odessa - Big Three | 1 |
| Morgan Creek - Odessa | Key - Lamesa | 1 |
| Moss Tr 1 | Odessa - Big Three | 1 |
| N Edinburg - Rio Hondo | Pharr - Pharr MVEC | 1 |
| N McCallen - N Edinburg | Polk - Pharr | 1 |
| N McCallen - S McCallen | Polk - Hall Acres | 1 |
| Nueces Bay - Whitepoint | Nueces Bay - Whitepoint | 1 |
| Odessa Switch - Moss | Holt Sw T1 | 1 |
| Odessa Switch - Moss | Odessa - Huntsman | 1 |
| Renner Sw - Tennyson | Allen Sw - Plano - Alma | 1 |
| Rio Hondo Tr | Rio Hondo - La Palma | 1 |
| Sargent - Watermill | Cedar Hill - Watermill | 1 |
| Stryker Creek - Trinidad | Watermill - Tricorner | 1 |
| Temple - Lake Creek/Tradinghouse | Bell City - Temple | 1 |
| Temple - Lake Creek/Tradinghouse | Robertson - Milano | 1 |
| West - North |  | 1 |
| West Levee Tr | Compton Road - Industrial Bvd | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

None

New Procedures/ Forms/ Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 08/26/2004 | ERCOT Power Operations Bulletin 109 | Temporary Change - Procedure When OOMEing Combined Cycle Units Off Line - Transmission & Security Desk |
| 08/26/2004 | ERCOT Power Operations Bulletin 108 | Temporary Change - Frequency Control Desk - South DC Tie |
| 08/26/2004 | ERCOT Power Operations Bulletin 107 | Transmission & Security Desk V2R26 - CN#152 |
| 08/25/2004 | ERCOT Market Operations Bulletin 18 | PRR 349 - UBES/DBES Deployment limitations due to Ramp Rate Recall |
| 08/25/2004 | ERCOT Market Operations Bulletin 17 | PRR 451 - Ancillary Services Obligations |
| 08/16/2004 | ERCOT Power Operations Bulletin 106 | Pre-Contingency Action Plans - Transmission & Security Desk |
| 08/16/2004 | ERCOT Power Operations Bulletin 105 | Day-Ahead Limit Calculation and Enforcement Practice Engineering Procedure |

# Security Alert Stage/ Threatcon/ Related issues

None

Major system voltage problems

None

Blackout/Load Shed incidences

None

# Communication

8/5 03:55 – 4:30 Portal inoperable

03:55 – 4:10 MOI inoperable

8/28 11:00- 11:25 Portal inoperable due to planned maintenance

Major Computer Problems & Fixes

# None

ERCOT peak (Unofficial)

8/3 17:00 58,590

## Max Temperature

8/4	103   Far West

OCN, Advisory, Alert, Emergency Notice and Major Events

| Transmission Alerts | San Angelo Area | Derby - Pearsall | Rio Hondo - Lapalma | Pleasonton Area | Asherton - West Conoco | Lon Hill Auto | San Miguel Area | Olson - Lake Whitney | Hanley - Duval | Hearne - Hearne City | El Dorado - Live Oak | Dansby - TAM | N Denton Tr | BriarCrest - Nall Lane | Navarro - Richland | Asherton - Eagle Pass | Ballinger - Paint Rock | Weslaco - N Weslaco | N McCallen - McColl Rd | Polk - Hall Acres | N Sanger - Spring | Rincon - Rockport | Cisco - Putnam |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 8/1 | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/2 | * | * | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/3 | * |  | * | * | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/4 | * |  |  |  | * | * | * | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/5 | * |  |  |  | * | * | * | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/6 | * |  |  | * |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/7 | * |  |  |  | * |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/8 | * |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/9 | * |  |  |  |  |  |  |  |  | * | * |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/10 | * |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/11 | * |  |  |  | * |  |  |  |  | * | * |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/13 |  |  |  |  | * |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |
| 8/14 |  |  |  |  |  |  |  |  |  |  | * |  | * |  |  |  |  |  |  |  |  |  |  |
| 8/15 | * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8/16 |  |  |  |  |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |
| 8/17 |  |  |  |  |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |
| 8/18 |  |  |  |  | * |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  |
| 8/19 | * |  |  |  |  | * |  |  |  |  | * |  |  | * |  |  |  |  |  |  |  |  |  |
| 8/20 | * |  |  |  |  |  |  |  |  |  | * |  |  | * | * | * | * | * |  |  |  |  |  |
| 8/21 | * |  | * |  |  |  |  |  |  |  | * |  |  | * |  |  | * |  | * | * |  |  |  |
| 8/22 |  |  | * |  |  |  |  |  |  |  |  |  |  | * | * |  |  |  |  | * |  |  |  |
| 8/23 |  |  |  |  |  |  |  |  |  |  |  |  |  | * |  | * |  |  |  | * |  |  |  |
| 8/24 | * | * |  |  |  |  |  |  |  |  |  |  |  | * |  | * |  |  |  |  | * | * |  |
| 8/25 | * | * |  |  | * | * |  |  |  |  |  |  |  | * |  |  |  |  |  |  | * | * |  |
| 8/26 | * | * |  |  | * | * |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  | * |  |
| 8/27 | * |  |  |  | * | * |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  | * |  |
| 8/28 | * |  |  |  |  |  | * |  |  |  |  |  |  | * |  |  |  |  |  |  |  | * |  |
| 8/29 |  |  |  |  |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |  |  | * |  |
| 8/30 |  |  |  |  | * |  |  |  |  |  |  | * |  |  |  |  |  |  |  |  |  | * | * |
| 8/31 |  |  |  |  |  |  |  |  |  |  |  |  |  | * | * |  |  |  |  |  |  |  | * |