## ERCOT Operations Report

## ROS & OWG

## October 2004

August Frequency control   59.9 > F > 60.1

Disturbances

| October Trips |  | MW Lost |
| --- | --- | --- |
| 10/3/2004 2:31 | 59.774 | 760 |
| 10/7/2004 10:50 | 59.878 | 290 |
| *10/7/2004 15:57 | 59.876 | 265 (3 CT's) |
| **10/7/2004 17:38 | 59.848 | 650 (3 Units) |
| 10/10/2004 20:28 | 59.826 | 610 |
| 10/15/2004 0:35 | 59.898 | 330 |
| 10/17/2004 15:57 | 59.880 | 380 |
| 10/21/2004 12:39 | 59.874 | 585 |
| 10/28/2004 17:43 | 59.898 | 465 |

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 10/1/2004 0:03 | 60.106 | 30518 | -44 | 709 | -1360 (-500) |
| 10/1/2004 22:05 | 59.893 | 38275 | 409 | -1437 | -5200 (-1050) |
| 10/2/2004 22:06 | 60.105 | 32464 | -856 | 480 | -2600 (-500) |
| 10/3/2004 3:03 | 60.101 | 24733 | -447 | 382 |  |
| 10/5/2004 22:08 | 59.876 | 33901 | 776 | -1465 | -3800 (-1090) |
| 10/6/2004 1:06 | 60.104 | 26480 | -354 | 624 | -1150 (-325) |
| 10/11/2004 5:59 | 60.117 | 24163 | -514 | -122 | 2950 (880) |
| 10/11/2004 6:06 | 59.871 | 24799 | -288 | -956 | 2950 (880) |
| 10/19/2004 7:36 | 60.147 | 35366 | -1100 | 515 | VDI to reduce generation. Incorrect Offset |
| 10/26/2004 5:59 | 60.119 | 29228 | -488 | 586 | 3500 (750) |
| 10/26/2004 22:06 | 59.889 | 36585 | 488 | -466 | -4700 (-970) |
| 10/31/2004 2:23 | 60.164 | 25130 | -650 | -210 | Frequency >60.05 for over 30 Minutes. VDI issued to reduce generation. |

Deployed Responsive  (38) (Reported Above)

| 10/1/04 6:05:10 | 10/8/04 0:01:06 | 10/15/04 6:07:40 | 10/22/04 0:04:12 |
| --- | --- | --- | --- |
| 10/1/04 10:04:40 | 10/8/04 6:09:30 | 10/15/04 17:33:12 | 10/22/04 6:42:36 |
| 10/1/04 22:02:32 | 10/8/04 8:04:34 | 10/15/04 20:15:56 | 10/26/04 22:02:46 |
| 10/2/04 22:49:30 | 10/8/04 13:48:26 | 10/17/04 11:21:44 | 10/27/04 23:06:00 |
| 10/3/04 2:31:56 | 10/10/04 20:28:42 | 10/17/04 15:57:56 | 10/28/04 17:43:12 |
| 10/4/04 6:09:30 | 10/11/04 6:04:18 | 10/17/04 18:52:20 | 10/29/04 6:10:22 |
| 10/5/04 22:03:20 | 10/11/04 22:35:10 | 10/19/04 6:05:54 | 10/30/04 2:18:48 |
| 10/7/04 10:50:52 | 10/12/04 6:10:34 | 10/20/04 0:33:10 | 10/31/04 8:02:30 |
| 10/7/04 15:57:30 | 10/12/04 22:12:14 | 10/20/04 6:11:18 |  |
| 10/7/04 17:38:46 | 10/15/04 0:35:54 | 10/21/04 12:39:46 |  |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Oct '03 | Sept '04 | Oct '04 |
| --- | --- | --- | --- |
| DFW | 173 | 88 | 68 |
| E RIO | 59 | 74 | 91 |
| W RIO | 32 | 56 | 60 |
| Laredo | 45 | 81 | 86 |
| Bryan Area | 0 | 23 | 55 |
| Corpus | 28 | 30 | 31 |
| Abilene | 39 | 30 | 28 |
| San Angelo | 34 | 30 | 11 |
| Western | 42 | 0 | 0 |
| Houston | 7 | 0 | 0 |
| San Antonio | 0 | 2 | 3 |
|  | 459 | 418 | 433 |

OOME / Congestion Management Activity

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| N Edinburg - Bates | McColl Rd - McCallen | 15 |
| Heights Sub - Freeway Park | Heights - PH Robinson | 13 |
| Citgo Oak Park - Highway 9 | Nueces Bay - Hiway 9 | 11 |
| Roanoke - Parker | Benbrook - Horne | 9 |
| South - Houston CSC |  | 9 |
| Gibbons Creek - Greens Prarie/East | TAMU - Dansby | 8 |
| Austrop - Sandow | Austrop Tr | 6 |
| Big Brown - Richland Chambers | Seagoville - Kleberg Tap | 6 |
| Ennis West - Sterret | Desoto - Red Oak | 6 |
| North - Houston CSC |  | 5 |
| Benbrook -Parker/Graham | Stephenville - Lingleville | 4 |
| Clear Springs - Marion/Zorn | SMI - McQueeney | 4 |
| Dilley Switch - San Miguel | Derbys - Pearsall | 4 |
| Gibbons Creek - Greens Prarie/East | Briarcrest - Nall Lane | 4 |
| La Palma - Rio Hondo | La Palma - Rio Hondo | 4 |
| Marion - Hill Country/Skyline | Seguin - Seguin West | 4 |
| Nueces Bay - Whitepoint | Nueces Bay - Whitepoint | 4 |
| STP - Skyline/Hill Country | Blessing - Lolita | 4 |
| Allen Renner/Tennyson | Allen Plano Alma Rd | 3 |
| Bates - Frontera | McCallen - McColl Rd | 3 |
| Big Brown - Richland Chambers | Navarro - Haney | 3 |
| Gibbons Creek - Greens Prarie/East | Jewet - Watsons Chapel | 3 |
| Gibbons Creek - Twin Oaks Switch | Jewet - Watsons Chapel | 3 |
| Barrilla - Ft. Stockton | Barrilla - Ft. Stockton | 2 |
| Big Brown - Richland Chambers | Trinidad TR 6H | 2 |
| Enterprise - Trinidad/Martin Lake | Nacadoches Tr | 2 |
| Henne - Comal | Seguin - Zorn | 2 |
| Live Oak - Sonora | El Dorado - Live Oak | 2 |
| Martin Lake - Tricorner/Elkton Forney Sw | Athens Tap - Athens | 2 |
| Menard Tr | Ballinger - Paint Rock | 2 |
| Morgan Creek - Eskota | Eskota Tr | 2 |
| Mt Enterprise - Trinidad / Martin Lake - Stryker Creek | Nacogdoches Tr | 2 |
| N McCallen - Frontera | Bates Tr | 2 |
| South - North CSC |  | 2 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Allen - Royse/ Monticello | Allen - Ben Davis | 1 |
| Asherton - Eagle Pass | Uvalde - Asphalt Mines | 1 |
| Barney Davis U1 | Arcadia - Southside | 1 |
| Bates U1 | McCallen - McColl Rd | 1 |
| Big Brown - Richland Chambers | Kleberg Tap - Southside WTP | 1 |
| Big Brown - Richland Chambers | Palestine - Elkhart | 1 |
| Big Lake - Friend Ranch | Midway Lane - Ozona | 1 |
| Burnet - Wirtz | Ferguson - Sherwood Shores | 1 |
| Cagnon - Marbach | Medical Center - Bandera | 1 |
| Calaveras- Skyline/Walzem Rd | Calaveras - Ball Park | 1 |
| Clear Springs - Marion/Zorn | Schertz - Parkway | 1 |
| Dezavala - Hill Country | Medical Center - Bandera | 1 |
| Fayetteville Tr | Gideon - Winchester | 1 |
| Fayetteville - Salem | Austrop Tr | 1 |
| Frontera - N McCallen | McColl Rd - McCallen | 1 |
| Gibbons Creek - Greens Prarie/East | Hearne - Hearne Cty | 1 |
|  | Greens Bayou Auto | 1 |
| Hood Tr | Spunky - Hood | 1 |
| Jewett Tr | Palestine - Elkhart | 1 |
| Kingsville - Alice | Calallen - Banquete | 1 |
| La Palma - Rio Hondo | McColl Rd - McCallen | 1 |
| Lon Hill - Whitepoint | Nueces Bay - Whitepoint | 1 |
| Marion - Hill Country/Skyline | Schertz - Parkway | 1 |
| Marshall Ford - Lago Vista | Ferguson - Sherwood Shores | 1 |
| Military Highway - Midtown | Loma Alta Tr | 1 |
| Morgan Creek - Odessa | Andrew N - Exxon Means Tap | 1 |
| Morgan Creek - Odessa | Odessa - Texas Jct Tap | 1 |
| Morgan Creek - Odessa | Texas Jct Tap - Sprayberry Sw | 1 |
| Mt Enterprise - Trinidad / Martin Lake - Stryker Creek | Athens Tap - Athens | 1 |
| N Edinnurg - Duke | N Edinburg - McColl Rd | 1 |
| N McCallen - N Edinburg | Bates - S Mission | 1 |
| N McCallen - N Edinburg | Wermser - Weslaco | 1 |
| N McCallen - W McCallen | Frontera - N McCallen | 1 |
| Northeast - North CSC |  | 1 |
| Odessa T2 | Odessa T1 | 1 |
| Olinger - Firewheel | Apollo Tr | 1 |
| Pedernales - Seaholm | Cardinal Lane - Zilker | 1 |
| Rio Hondo Tr | Rio Hondo - La Palma | 1 |
| San Angelo - Concho | San Angelo St. - Live Oak | 1 |
| STP WA Parrish | Biport - Richwood | 1 |
| Uvalde - Hamilton | Asherton - West Conoco | 1 |
| Westside - Airline | Arcadia - Southside | 1 |
| Zorn - Lytton Springs/Austrop | Canyon -Rohr | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

None

New Procedures/ Forms/ Operations Bulletins

| 10/27/2004 | ERCOT Power Operations Bulletin 117 | Temporary Change - Transmission & Security Desk CN#161 |
| --- | --- | --- |
| 10/11/2004 | ERCOT Power Operations Bulletin 116 | Transmission & Security Desk V3R28 - CN#162 |
| 10/06/2004 | ERCOT Power Operations Bulletin 115 | Transmission & Security V3R27 - CN#157 |
| 10/01/2004 | ERCOT Power Operations Bulletin 114 | Revision to Shift Supervisor V3R9 |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems

None

Blackout/Load Shed incidences

None

# Communication

10/14	18:40	Portal Inoperable.  Deployments sent manually.

10/19  09:52 – 17:10 MOI experiencing intermittent failure.

10/22 	Held 11:45 Interval

Major Computer Problems, Enhancements & Fixes

# 10/5	15:00  Outage Scheduler enhancements placed in production.

ERCOT peak (Unofficial)

10/20		48,225

OCN, Advisory, Alert, Emergency Notice and Major Events

|  | San Angelo - Menard loads Ballinger - Paint Rock | Menard Tr loads Ballinger - Paint Rock | Jewett Tr loads Palestine - Elkhart | Jayton - Jayton CSW loads Spur - Girard | Dilley - San Miguel loads Derby - Pearsall | Uvalde - Hamilton loads Asherton - West Conoco | Asherton - Eagle Pass loadsUvalde - Asphalt Mines | Sonora - Hamilton oad loads Asherton - Conoco | Hood Tr loads Spunky - Hood | Live Oak - Sonora laods El Dorado - Live Oak | Gibbons Creek - Bryan East/Greens Prarie loads BriarCrest - Nall Lane | N Edinburg - Bates loads N McCallen - McColl Rd | Kingsville - Alice loads Calallen - Banquete | (Contingency loads Element) | Transmission Alerts |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10/1 |  |  |  |  | * |  |  |  |  |  |  |  |  |  |  |
| 10/2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/5 |  |  |  | * |  |  |  |  |  |  |  |  |  |  |  |
| 10/6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/8 |  |  |  |  |  | * | * |  |  |  |  |  |  |  |  |
| 10/9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/11 |  |  |  |  |  |  |  |  |  | * |  |  |  |  |  |
| 10/12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/17 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/18 |  |  |  |  | * |  |  |  |  |  | * | * |  |  |  |
| 10/19 | * |  |  |  | * |  |  |  |  |  | * | * |  |  |  |
| 10/20 | * |  | * |  | * |  |  |  | * | * | * | * |  |  |  |
| 10/21 |  |  |  |  | * |  |  |  | * |  | * | * |  |  |  |
| 10/22 |  | * |  |  |  |  |  |  |  |  | * | * |  |  |  |
| 10/23 |  | * |  |  |  |  |  | * |  |  |  |  |  |  |  |
| 10/24 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/25 |  |  |  |  |  |  |  |  |  |  |  |  | * |  |  |
| 10/26 |  | * |  |  |  |  |  |  |  |  |  |  | * |  |  |
| 10/27 |  |  |  |  |  |  |  |  |  |  |  |  | * |  |  |
| 10/28 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/29 |  |  |  |  | * |  |  |  |  |  |  | * |  |  |  |
| 10/30 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10/31 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |