# SPWG Report to ROS

#### November 9th, 2004

By December 31, 2004, SPWG member companies to complete the loadability evaluation of zone 3 relays on lines rated 230 kV and above, in accordance with NERC recommendation 8a, using the winter 4 hour emergency ampere rating in the evaluation. Members to identify relays that do not meet the criteria and either a) file a request for exemption with ERCOT compliance or b) provide a plan to modify or replace relays that do not meet the criteria.

SPWG members have agreed that the present work environment better supports compilation of future year short circuit databases starting in April rather than late summer. SPWG Procedures have been modified to reflect the revised schedule and sent to SPWG members for review. Any comments will be discussed at the November SPWG meeting and the document should be ready for ROS consideration at the December ROS meeting.

Disturbance monitoring equipment location criteria presently applies to equipment operated at 60 kV or above. This is a change from wording previously approved by the SPWG specifying 100 kV and above. SPWG members agree reference to 60 kV should be revised to 100 kV. An OGRR will be prepared.

The next SPWG meeting is scheduled for November 18th and 19th, 2004, in Houston.

Jack Dahnke

SPWG Chair