10/21/04

Comment Summary and ERCOT response

Subject:  Elm Creek Switching Station Project

| Entity | Comments | ERCOT Response |
| --- | --- | --- |
| All | No comments objecting to project | ERCOT staff concurs |
| LCRA TSC | Replace 10 345-kV circuit breakers at the Marion switching station. The construction of the 345-kV Elm Creek switching station increases the available fault current at the Marion 345-kV switching station. The approximate cost estimate for replacing these 10 circuit breakers is $4.5M. LCRA recommends that the Elm Creek switching station be designed to accommodate the addition of 345/138-kV autotransformer capacity at this site in the future. The location of this switching station offers an excellent site to support future load growth in this area. | ERCOT staff concurs |
| TXU Energy | Due to the significant benefit of adding a 0.04 p.u. series reactor in the Marion – Skyline 345 kV Line (page 11), TXU Energy would like to see this included, and approved as a part of the overall Elm Creek project. | Reactor suggestion will require further study and may be added as separate project in the future. This would be the first application at 345 kV operating voltage and dynamic and TRV studies may be needed. |