## ERCOT Operations Report

## ROS

## November 2004

November Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 11/1/2004 0:06 | 60.130 | 27929 | -521 | -114 | Frequency >60.05 for over 30 Minutes. VDI issued to reduce generation. |
| 11/1/2004 8:37 | 60.114 | 32154 | -872 | 278 | VDI issued to reduce generation |
| 11/1/2004 23:06 | 60.107 | 27177 | -944 | 509 | -2000 ( -500) |
| 11/2/2004 0:03 | 60.103 | 25292 | 43 | 312 | -2175 ( -400) |
| 11/3/2004 23:09 | 60.114 | 26413 | -306 | 779 | -1450 (-550) |
| 11/4/2004 1:56 | 60.104 | 23927 | 110 | 740 |  |
| 11/5/2004 6:33 | 60.105 | 30520 | -192 | 99 | Low frequency 06:08 -06:20 |
| 11/5/2004 17:54 | 59.895 | 30639 | 1000 | -209 | Evening load pickup higher than expected. |
| 11/6/2004 8:37 | 60.105 | 27027 | -768 | 239 |  |
| 11/7/2004 9:34 | 60.103 | 25804 | -146 | -82 |  |
| 11/7/2004 14:15 | 60.109 | 29089 | -187 | 314 |  |
| 11/10/2004 0:04 | 60.133 | 24136 | -227 | 359 | -600 ( -350) |
| 11/11/2004 0:45 | 60.119 | 23791 | -520 | 181 |  |
| 11/12/2004 7:02 | 60.122 | 31004 | -867 | 66 | Three VDIs issued to reduce generation |
| 11/12/2004 8:34 | 60.137 | 31225 | -486 | 157 |  |
| 11/13/2004 14:11 | 60.101 | 28449 | 188 | 232 |  |
| 11/16/2004 10:33 | 59.897 | 30602 | -225 | -125 |  |
| 11/21/2004 13:47 | 59.873 | 28823 | -32 | -82 | Frequency dipped to 59.87 and immediately recovered. RRS deployed. Storms in Austin & Houston |
| 11/26/2004 5:58 | 60.105 | 25517 | -920 | 956 | 2350 (750) |
| 11/30/2004 7:40 | 60.127 | 34379 | -868 | -59 | Issued 2 VDI's to reduce generation. |
| 11/30/2004 18:13 | 60.116 | 37286 | -906 | 332 | VDI issued to reduce generation |

Disturbances

| November Trips |  | MW Lost |
| --- | --- | --- |
| 11/4/2004 3:00 | 59.803 | 530 |
| 11/4/2004 3:05 | 60.105 | Overshoot from trip |
| 11/5/2004 10:59 | 59.898 | 205 (2 units) |
| 11/5/2004 21:17 | 59.801 | 775 |
| 11/8/2004 12:33 | 59.893 | 170 MW pre disturbance frequency 59.93 |
| 11/10/2004 13:51 | 59.787 | 750 |
| 11/14/2004 3:13 | 60.102 | Load loss (LAAR) |
| 11/17/2004 10:33 | 59.814 | 660 (3 units) |
| 11/17/2004 19:48 | 59.872 | 300 (2 units) |
| 11/18/2004 17:40 | 59.861 | 375 |
| 11/18/2004 17:48 | 59.863 | 605 (2 units) |
| 11/20/2004 21:36 | 59.845 | 570 |
| 11/20/2004 21:47 | 60.107 | Overshoot from trip |
| 11/21/2004 21:53 | 59.864 | 500 |
| 11/26/2004 3:48 | 59.897 | 250 (2 units) |
| 11/29/2004 23:47 | 59.849 | 520 runback and trip |
| 11/30/2004 14:35 | 59.836 | 550 |

Deployed Responsive  (57) (Reported Above)

| 11/1/04 0:32:20 | 11/6/04 14:35:24 | 11/17/04 19:47:58 |
| --- | --- | --- |
| 11/2/04 2:13:36 | 11/6/04 17:36:22 | 11/18/04 6:07:18 |
| 11/2/04 6:04:40 | 11/6/04 17:56:36 | 11/18/04 17:40:06 |
| 11/2/04 12:37:36 | 11/7/04 21:33:56 | 11/18/04 17:48:22 |
| 11/2/04 21:58:10 | 11/8/04 9:09:42 | 11/19/04 6:12:10 |
| 11/3/04 8:04:44 | 11/8/04 12:32:56 | 11/19/04 17:11:22 |
| 11/3/04 18:36:14 | 11/8/04 17:31:32 | 11/20/04 21:36:30 |
| 11/3/04 21:58:20 | 11/9/04 14:36:04 | 11/20/04 21:58:42 |
| 11/4/04 3:00:04 | 11/10/04 5:01:34 | 11/21/04 13:47:52 |
| 11/4/04 6:08:44 | 11/10/04 13:51:26 | 11/21/04 21:53:20 |
| 11/4/04 7:48:08 | 11/13/04 6:03:52 | 11/22/04 17:23:20 |
| 11/4/04 22:05:40 | 11/13/04 6:13:16 | 11/23/04 6:55:24 |
| 11/5/04 6:13:32 | 11/14/04 17:03:48 | 11/26/04 3:48:50 |
| 11/5/04 10:59:26 | 11/14/04 17:09:32 | 11/29/04 22:05:46 |
| 11/5/04 17:48:30 | 11/15/04 23:28:00 | 11/29/04 23:47:04 |
| 11/5/04 21:17:44 | 11/16/04 6:06:02 | 11/30/04 14:35:14 |
| 11/5/04 22:05:54 | 11/16/04 10:33:06 | 11/30/04 17:04:10 |
| 11/6/04 0:07:10 | 11/16/04 15:06:20 | 11/30/04 20:08:44 |
| 11/6/04 12:02:32 | 11/17/04 10:31:36 | 11/30/04 21:58:50 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Nov '03 | Oct '04 | Nov '04 |
| --- | --- | --- | --- |
| DFW | 105 | 68 | 7 |
| E RIO | 49 | 91 | 57 |
| W RIO | 36 | 60 | 29 |
| Laredo | 34 | 86 | 40 |
| Bryan Area | 4 | 55 | 6 |
| Corpus | 29 | 31 | 30 |
| Abilene | 58 | 28 | 30 |
| San Angelo | 55 | 11 | 0 |
| Western | 22 | 0 | 0 |
| Houston | 10 | 0 | 0 |
| San Antonio | 0 | 3 | 0 |
|  | 402 | 433 | 199 |

OOME / Congestion Management Activity

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Heights Sub - Freeway Park | Heights - PH Robinson | 14 |
| Clear Springs - Marion/Zorn | SMI - McQueeney | 13 |
| N Edinburg - Bates | Polk - Hall Acres | 7 |
| Big Brown - Richland Chambers | Trinidad TR 6H | 4 |
| N Edinburg - Rio Hondo | Weslaco - N Weslaco | 4 |
| STP - Skyline/Hill Country | Blessing - Lolita | 4 |
| Austrop - Lost Pines | Winchester - Fayetteville | 3 |
|  | Spunky - Hood | 3 |
| Duke - N Edinburg | Pharr - Pharr MVEC | 2 |
|  | South - North CSC | 2 |
| Steephollow - Gibbons Creek | Jewet - Watsons Chapel | 2 |
| Uvalde - Hamilton | Asherton - West Conoco | 2 |
| Argyle - Valley View | N Denton T1 | 1 |
|  | Asherton - W Conaco | 1 |
| Austrop - Sandow | Austrop Tr | 1 |
| Baytown Energy - Chambers | Baytown Energy - Chambers | 1 |
| Crane - Midkiff | Sw Mesa - Big Lake | 1 |
| Dilley Switch - San Miguel | Derbys - Pearsall | 1 |
| Duke - N Edinburg | Weslaco- Heidelburg | 1 |
| Ennis West - Sterret | Desoto - Red Oak | 1 |
| Gibbons Creek - Greens Prairie/East | Booneville - Carlos Sw | 1 |
| Gibbons Creek - Twin Oaks Switch | Jewet - Watsons Chapel | 1 |
| La Palma - Rio Hondo | La Palma - Rio Hondo | 1 |
| Lamesa - Bluff Creek | Moss Switch - Amaco N Cowden Tap | 1 |
| Lon Hill - Whitepoint | Nueces Bay - Whitepoint | 1 |
|  | McCamey Area voltage | 1 |
| N Denon Tr | Sanger - Spring | 1 |
| N Edinburg - McColl Rd | Polk - Hall Acres | 1 |
| Rio Hondo Tr | Rio Hondo - La Palma | 1 |
| S Lane City - Lane City | Columbus - Stafford Hill | 1 |
| San Miguel Tr | Derbys - Pearsall | 1 |
|  | Sandow Tr. | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

None

New Procedures/ Forms/ Operations Bulletins

| 11/04/2004 | ERCOT Power Operations Bulletin 120 | Temporary Change - Transmission & Security Desk CN#166 |
| --- | --- | --- |
| 11/02/2004 | ERCOT Power Operations Bulletin 119 | Shift Supervisor V3R11 - CN#164 |
| 11/01/2004 | ERCOT Power Operations Bulletin 118 | DC Ties V1R5 - CN#165 |

Major system voltage problems

11/8 and 11/9 Fluctuating 138 kV voltages observed in the McCamey area during increased wind farm generation.

Blackout/Load Shed incidences

11/24	Approximately 150 MW of distribution load lost due to storms.

# Communication

11/19 16:30 – 19:00	Lost Hot Line communications with a QSE.

11/26  03:00	Held interval due to an incorrect offset entered.

11/29 15:00	Extended the Ancillary Service Market until 17:00.

Major Computer Problems, Enhancements & Fixes

None

ERCOT peak (Unofficial)

11/29 	37,900

OCN, Advisory, Alert, Emergency Notice and Major Events

11/1	12:00-21:00	Transmission Alert.  Loss of Bates U1 loads Bates Tr.

13:00-21:00	Transmission Alert.  Loss of Rio Hondo Tr loads Rio Hondo – La Palma.

11/1-11/4		Transmission Alert.  Loss of Highway 9 Tr. loads Koch Up River - Valero.

11/10	08:00-15:00	OCN issued for notification of winter preparedness drill.

11/22 	16:45-17:45	Transmission Alert.   Loss of Dilley Sw – San Miguel loads Derby – Pearsall.

11/25	03:45-16:50	OCN issued to request QSE’s to update load forecast and resource plans for

HE 10:00 and 11:00.

11/26   16:50-18:00	Transmission Alert.  Loss of N Edinburg – Bates loads McColl Rd – N McAllen.

11/29   19:00-22:45	Transmission Alert.  Loss of N Denton – W Denton loads Sanger – Spring.

19:00-22:00	Transmission Alert.  Loss of Military Park Tr #2 loads Military Park Tr #1.