## Slide 1: August 18th DCS Event November 4, 2004 TAC Meeting

## Slide 2: NERC DCS Standard
DCS measures a Control Area’s ability to utilize its Contingency Reserves following a Reportable Disturbance. (NERC Policy 1B)
Reportable Disturbances are contingencies 80% - 100% of the most severe single contingency loss.
ERCOT’s most severe single contingency is defined as losing one STP Unit rated at 1250 MW.
Frequency must return to 60 Hz, or the pre-disturbance value if below 60 Hz just prior to the disturbance, within 15 minutes.

## Slide 3: DCS History
Since 2000 ERCOT has recorded 16 reportable events and 5 non-reportable events.
Recovery time since single control area operations began has averaged 6.5 ~ 7.0 Minutes (excluding the Aug 18th event)

## Slide 4: August 18th Event
For interval ending 10:15, QSEs had an overall increase of 2,746 MW of Scheduled Generation from the previous interval.
ERCOT load forecast indicated excess generation so 1,893 MW of Down Balancing was deployed.
At 9:59:20, about halfway through the normal 10-minute ramp period, a transmission disruption led to a loss of 1115 MW at two generation facilities.
Frequency dropped to 59.77 Hz
Recovery began normally, but stalled after 9 minutes.
60 Hz frequency reached after 17.3 minutes.

## Slide 5
Frequency

## Slide 6: Ancillary Service Deployments

## Slide 7
August 18th Vs. August 19th
August 18th
  Time of event was 9:59:20
  Recovery time of 17.37 minutes
  1115 MWs Lost
August 19th
  Time of event was 11:08:16
  Recovery time of 8.23 minutes
  1247 MWs Lost

## Slide 8: August 19th DCS Event

## Slide 9: Further Investigation
Review ERCOT Operator Response to DCS events
Review QSE Non-Performance
Review Governor Response
Evaluate the amount of Generation RRS Deployed by the system.

## Slide 10: DCS Penalty
Percent recovery 15 minutes (Aug 18) 82.5%
Percent recovery 15 minutes (Aug 19) 100%
Quarterly Average (2 events) 91.3%
3 Month Contingency Reserve Increase 109 MW