## Slide 1: South Region Transmission Project: Elm Creek 345 kV Switching Station
Presentation to TAC at their
November 4, 2004 meeting by
ERCOT Transmission Services Operations

## Slide 2: Problem
Local Area Congestion Management resulted in over $14 million in additional costs
Due to reliability limits in the 138 kV infrastructure northeast and east of San Antonio
  Remedial Action Plan in place for contingent loss of Marion to Hill Country/Skyline

## Slide 3: Solution
Regional Planning Groups continue to examine both short and long term solutions for the Central Texas Area
Short Term solution
  Reconfigure grid by building a new 345 kV Switching Station at the intersection of Marion-Hill Country/Skyline and Marion-San Miguel 345 kV lines
    Eight 345 kV terminals
    Includes long term planning capability to add 345/138 kV autotransformer and two 138 kV circuits to support load growth
  Upgrade Marion Circuit Breaker Capability
  Continue examination of 345 kV Series Reactor

## Slide 4: Location

## Slide 5: Costs
$4 to $11 Million Dollars Per Year Production Cost Savings
  Dependent on status of generation in Central Texas
Total Estimated Capital Cost of Project
  $16.5 million ($2.72 million annual TCOS)
Net savings are $1.3 to $8 million per year

## Slide 6: Comments
Company | For/Against | Comments
LCRA | For | Replace 10 CB’s at Marion. Add future 345/138 kV Auto and 2 138 kV exit circuits
TXU Energy | For | Add 0.04 pu series reactor to Marion – Skyline 345 kV line.

## Slide 7: Questions?