## Slide 1: Event Summary
1103.59 MW of generation tripped during first minute beginning at 09:59:22.
All 930 MW of reg up deployed plus 49.47MW of down reg recalled by 10:09:02
801.27 of Responsive Deployed to generators by 10:01:50
172.1 MW of LaaR tripped.

## Slide 2: Evaluation of Responsive Reserve Providers 10 minutes after Responsive Deployed
QSE’s that under-generated were 412.11 MWs short.
QSE’s that over-generated were 306.75 MWs over.
Net shortage of Responsive Reserve providers was 105.36 MWs

## Slide 3: Evaluation 10 Minutes after Responsive Deployed
Frequency at 10 minutes 59.906 Hz
ERCOT measured Bias this event: 530 MW/0.1 hz
Estimate additional generation needed for 60 Hz as 498.2 MW
Responsive providers were 105.36 MWs short
Non Responsive providers were 4.53 MW over their obligations
QSE’s net shortage was 100.83 MW
If net shortage was 0 MW, Hz would have been 59.925 Hz.
If no Responsive Reserve provider under generated, Hz would have been 59.9837 Hz (keeping the 307 over generation)

## Slide 4: Evaluation of Responsive Reserve Providers 15 Minutes after beginning of Event – DCS time limit
QSE’s that under-generated were 283.47 MWs short.
QSE’s that over-generated were 188.97 MWs over.
Net shortage of Responsive Reserve providers was 94.5 MWs

## Slide 5: Evaluation 15 Minutes after Responsive Deployed
Frequency at 15 minutes 59.955 Hz
ERCOT measured Bias this event: 530 MW/0.1 hz
Estimate additional generation needed for 60 Hz as 238.5 MW
Responsive providers were 94.5 MWs short
Non Responsive providers were 26.26 MW over their obligations
QSE’s net shortage was 68.24 MW
If net shortage was 0 MW, Hz would have been 59.968 Hz.
If no Responsive Reserve provider under generated, Hz would have been 60.000 Hz (keeping the 189 over generation)

## Slide 6: ERCOT Load
ERCOT Load growth at 52.4 MW/min (avg). Balancing Deployments and Base Schedules averaged 47.5 MW/min. This resulted in about 52 MWs short during event. This had to be made up by Regulation.
RTU failure caused load calculation to be incorrect.

## Slide 7: Performance Summary

## Slide 8: Ancillary Deployments

## Slide 9: SCE 1

## Slide 10: SCE 2

## Slide 11: SCE 3

## Slide 12: SCE 4

## Slide 13: SCE 5

## Slide 14: SCE 6