- Dynamics Working Group

#### PROCEDURAL MANUAL

## TABLE OF CONTENTS

- Foreword

- Introduction

- Data Requirements

- New Dynamics Data

- Revising Dynamics Data

- High Set Under-Frequency Load Shedding Data

- Firm Load Under-Frequency Load Shedding Data

- Under-Voltage Load Shedding Data

- Protective Relay Data

- Missing Dynamics Data

- Dynamics Data Screening Procedures

- Annual Data Filing and Distribution

- Dynamics Data Base

- Stability Book

- Annual Dynamics Data Update Schedule

- Procedural Manual Revisions Guidelines

- Flat Start Tutorial

- Dynamics Working Group  Roster

- FOREWORD

This Procedural Manual is intended for use by the stakeholder members of the Electric Reliability Council of Texas (ERCOT) for the purpose of creating and maintaining the dynamics database and dynamics simulation cases which are used to evaluate the dynamic performance of the ERCOT system.

The majority of ERCOT member utilities utilize Power Technologies Inc. (PTI) Power System Simulator (PSS/E) software.  Consequently, the various activities in the procedural manual incorporate PTI procedures and nomenclature in describing these activities. Wherever possible, a description of the PTI activity is given so users of software other than PTI may implement similar actions.

Section II of this Procedural Manual describes the data requirements for the modeling of generation associated equipment for use in dynamics studies.  This section also describes the requirement for documentation of revisions to existing dynamics data.

Sections III and IV of this Procedural Manual describes the basic procedures for the screening and checking of dynamics data before it is submitted to  ERCOT System Planning (ESP) to start the annual dynamics data base update.

Section V describes the annual dynamics data update schedule.  Section VI contains guidelines to review the Procedural Manual.

Section VII contains a Flat Start Tutorial.

INTRODUCTION

To adequately simulate the behavior of the ERCOT system it is necessary to develop and maintain dynamic simulation-ready base cases and associated dynamics data files using actual equipment data together with appropriate dynamic simulation software.  The ERCOT Steady State Working Group (ERCOT-SSWG) power flow cases provide transmission system representations which, along with the dynamics database, are used by the Dynamics Working Group (DWG) to create dynamic simulation cases ready to run under PTI’s PSS/E v.29 software.

DWG members are responsible for submitting dynamics data revisions or additions to ERCOT System Planning (ESP). Each ERCOT area, as defined in the base case, shall have a data owner who is responsible for submitting all the dynamic data required by DWG for that area. Such a data owner should be identified in the DWG members list in an annual basis and updated as needed.  ESP receives updates from the working group and updates the ERCOT dynamics database.  The newly revised ERCOT dynamics database is then released to the Working Group Chair.  Then dynamic simulation cases for the current year and a future year determined annually by the Working Group are created.  This process is repeated annually.

### DATA REQUIREMENTS

### A.  New Dynamics Data

The DWG utilizes the ERCOT dynamic data set to collect dynamics data for new generation equipment. This data set include a dyr file, in CSV format, with models for generators, exciters, turbine governors, stabilizers and auxiliary files (idv files for use with PTI software) that modify the base case to pair it with the dynamic data.

The idv files to be prepared are:

| XX_gnet.idv | to net generation for lack of dynamic data |
| --- | --- |
| XX_zsorce.idv | to modify the zsorce value |
| XX_conl.idv | to modify dynamic load conversion |
| XX_network.idv | for other modifications to the network |

where XX is an identifier with the tdsp, the year and the base case name, i.e. CPS_03sum1.

### B.  Revising Dynamics Data

For revisions to the existing dynamics data, the DWG utilizes the previous year dynamics data set emailed by ESP.  Each member2 submits to ESP revisions in their dyr file and on the idv files. Changes to existing data should typically occur only after modifications of generating units. Examples are replacement of an old excitation system with a new, static excitation system and boiler/turbine modification. Extreme care should be taken in changing the dynamic data to match originally submitted manufacturers’ data. The dynamic data has been tuned to ensure proper operation of the models and original manufacturers’ data may have been modified during this process. Obsolete data should be deleted.

# C. High Set Under-Frequency Load Shedding Data

A high set under-frequency load shedding (Hi-set UFLS) relay data is to be reviewed and maintained by DWG and submitted to ESP on a yearly basis at the same time the new dynamic data is submitted.  The data shall be formatted into a PTI model that contains the necessary information for dynamic studies to properly represent the High-Set UFLS relay action.

# D. Firm Load Under-Frequency Load Shedding Data

An under-frequency load shedding (UFLS) relay data for firm load is to be reviewed and maintained by DWG and submitted to ESP on a yearly basis at the same time the new dynamic data is submitted.  The data shall be formatted into a PTI model that contains the necessary information for dynamic studies to properly represent the UFLS relay action.

One PTI model available for such use is “LDSHXX”.  LDSHXX is defined in the PTI Program Operation Manual – Volume II under the CONEC and CONET Model Data Sheets.  The LDSHXX model is summarized as follows:

LDSHXX (Under Frequency Load Shedding Relay Model):

I,’LDSHXX’, LID, F1, T1, Frac1, F2, T2, Frac2, F3, T3, Frac3, TB/

where:

I	= Bus Number, owner number, zone number, area number

XX	= BL (bus), OW (owner), ZN (zone), AR (area)

LID	= Load ID

F1,2,3	= Load Shedding Points (Hz)

T1,2,3	= Pickup Times (Seconds)

Frac1,2,3	= Fractions Of Load To Be Shed

TB	= Breaker Time (Seconds)

Note:  Other load shedding relay models are available in the PTI manual.

# E. Under-Voltage Load Shedding Data

An under-voltage load shedding relay data is to be reviewed and maintained by DWG and submitted to ESP on a yearly basis at the same time the new dynamic data is submitted.  The data shall be formatted into a PTI model that contains the necessary information for dynamic studies to properly represent the UV relays action.

- F. Protective Relay Data

The operation of protection, control, and special protection systems can affect the dynamic performance of the ERCOT system during and following contingencies. Planning, documenting, maintaining, or other activities associated with these systems is outside the scope of the DWG. However, because they can affect dynamic performance, the DWG should, on an as needed basis, identify and document protection, control, and special protection systems, which affect multiple transmission providers. Identification activities will normally require the assistance of individuals or groups outside the DWG. The specific information to be considered for inclusion will depend on the type, purpose, and scope of study.

Protection, control, and special protection systems included in the DWG database, or book, should be in the form of a standard PTI model or models. A descriptive model, such as a time-based sequence of events, is also acceptable. Protection, control, and special protection systems adequately modeled for dynamic purposes by other working groups only need to be referenced in the DWG book.

The PTI software contains several models, such as OSSCAN and RELAY1, which may be used to indicate situations where actual protection, control, and special protection systems should be included in a simulation (After PSS/E Rev. 28, such models are replaced with “simulation calculation options”. See Program Operations Manual Vol. 1 Section 5.31.).

The DWG member, as part of the annual database update, should add identified protection, control, and special protection systems to the DWG database, or book. The DWG member, as part of the annual database update, shall review and update as necessary protection, control, and special protection systems already in the DWG database, or book. This review should include evaluating the existing data for applicability and accuracy. Obsolete data should be deleted. Both additions and updates are due when the high set under frequency relay scheme updates are due.

- Missing Dynamics Data

DWG shall procure and model as much dynamic data as needed for the several engineering studies that it is charged with.  Each DWG member shall provide a list of dynamics devices without the appropriate dynamic data and recommendations on how to cope with such lack of data.  DWG should identify and document missing dynamics data, models, protection data, and special protection systems, for which data is not currently available. Identification activities will normally require the assistance of individuals or groups outside the DWG.

DYNAMICS DATA SCREENING PROCEDURES

Each DWG member must perform dynamics data screening before submitting it to ESP. Included in the data screening check should be as a minimum the items listed and described below.

A. The dynamics data provided should be actual equipment data.  The database is developed as much as possible with actual dynamics data.  This includes generator, step-up transformer, excitation system, turbine, and governor models as well as other models (load, stabilizers, relays, etc.). The actual equipment data is derived from field testing or manufacturer data sheets. Conventional machines for which complete data is unavailable should be modeled using generator models like GENROU or GENSAL with typical data. If no data on the excitation system is available, PSS/E has a special excitation system, SEXS, provided for this purpose. Refer to the Program Application Guide, Volume 2, Section 21.2.3. Classical data is not acceptable.

B. DWG format is compatible with SSWG power flow models. Currently, the SSWG power flow models are developed using the PTI format.

C. Units and plants should be represented as follows:

- Units should not be lumped together.

- Unit’s step-up transformer should be modeled explicitly.

- Unit’s total Qmax should not contain external power factor correction capacitors netted into it.  Such capacitor should be modeled explicitly in the Switched Shunt data block of the base case.

- Plants with total generation less than 50 MVA may be netted out.

D. Each unit should have consistent unit identifiers (1-9, A-Z).

Unit identifiers should be consistent from year to year.  PTI format allows one two character alpha-numeric field.

E. Dynamics data must be provided in machine MVA base.

  - Each unit data must be supplied using its own machine base as represented in the SSWG power flow cases.  The machine kV base must also be represented correctly.

  - Zsource data provided in the SSWG power flow cases must match the dynamics data. Zsource must be the unsaturated subtransient reactance of the machine (Xdi”) for GENROU, GENSAL, GENDCO AND FRECHG models and must be the transient reactance Xd’ for the GENTRA and GENCLS models.

F. Units not dispatched must be modeled with a status "0", or off-line, in the power flow model. Units that are not dispatched should have dynamics models and data in the dynamics database for completeness of data as well as to simulate other scenarios.

G. Unit data checks.

- Realistic values (Actual values determined from unit testing should be used whenever possible) should be used for Pmin, Pmax, Qmin, and Qmax. The Pmax value in the dynamics data should match the Pmax value used in the load-flow data. Use of default values is not acceptable for both power flow and dynamics data.

- Screening checks shall be performed on the power flow model used in association with the dynamics data. The following are examples of screening checks to be performed.

    - Pgen + jQgen <= 115% of MVA base

    - Qmax >= Qmin.

    - Z source data provided in the SSWG power flow must match the dynamics data.

  - Screening checks shall be performed on the dynamics data. The following are examples of screening checks to be performed.

    - Inertia constant should include both turbine and generator.

    - Generator reactance data is unsaturated.

    - Refer to the Program Application Guide, Volume 2, Chapter 21 for use of activities DOCU, ESTR, ERUN, GSTR, and GRUN in data screening.

H. Station service/auxiliary load representation at the generation bus is recommended.

I. User defined models.

DWG is also charged to build a dynamics data set that is convertible to different formats.  When a PTI user provides user defined models, these models will need to be converted for use in other programs.  Standard models should be provided along with the user defined models.  The data are to contain the following items.

- Standard PTI models

- User defined models with associated Fortran code

- Approximations of user written models in PTI/standard format

J. Members must perform initialization of data with no errors and demonstrate that simulation output channels do not change for a ten second run with no disturbance prior to submittal to ESP.

K. Load models for P + Q should be provided.

Appropriate load models i.e., percentage of constant P, Q, I, & Z should be provided by each company. Further detailed load data, like large motors, small motors, discharge lamps, pure resistive and transformer excitation current, may be required for specialized dynamic studies and members are encouraged to compile them.

Reactive power values of loads should not include the value of the power factor correction capacitor. Such capacitor should be modeled explicitly in the Switched Shunt data block of the base case.

### Annual Data Filing and Distribution

- A. Dynamics Data Base

Once the flat start for the required load flow cases has been completed, the dynamics data is distributed to each of the DWG members electronically in PTI format.  This dynamic data distribution must be within the schedule stated in the DWG Procedures.

B. Stability Book

The stability book is used to document dynamics data changes and/or corrections required during the flat start process. Recommendations to revise load flow data are also included in the book. DWG Members are required to communicate these recommendations to their respective SSWG member to eliminate recurring problems.

To verify the successful completion of the flat start process, this book should also contain plots of the flat start results. The plots should include, at a minimum, the six (6) worst units (based on angle deviation).

The dynamics data is also included in the stability book. This data is in the DOCU ALL PTI format.

Also included in the stability book is the load shedding relay data submitted by each of the appropriate Dynamics Working Group members.

### Annual Database Update Schedule

- ESP Letter

By  __________, the ESP will send a letter to all power source owners reminding them to submit any dynamics model or data changes to the affected DWG member. The information will be due on __________.

- Model and data review by DWG members

DWG members are the recipients of dynamics models and data. The information received should be reviewed for completeness and applicability as described in sections III and IV of this procedure. The data should be appropriate for the model, and the model should be appropriate for the equipment.  The ‘ERCOT Modeling Guide for Dynamic Stability’ provides additional information about modeling. If there are questions or problems, the DWG member should discuss and resolve them with the power source owner.  This data review should be completed and data submitted to ESP by _________.

- ESP Flat Start

ESP will add all of the updates to the ERCOT dynamics database and perform a flat start as described in section VII of this procedure. ESP will contact the appropriate DWG member to resolve any problems with the data encountered during the flat start process. The updated database will be completed by January 15.

PROCEDURAL MANUAL REVISIONS

The DWG is responsible for maintaining and updating this PROCEDURAL MANUAL. Revisions, additions and/or deletions to this PROCEDURES MANUAL may be undertaken at such times that the DWG feels it is necessary due to changes in PTI dynamic simulation software or to meet new and/or revised requirements of NERC, ERCOT or any other organization having oversight or regulatory authority.

At least annually, the DWG Chair shall notify the DWG requesting each member to make a thorough review of the current PROCEDURAL MANUAL for any needed revisions. The notification will request that proposed revisions be submitted to the DWG Chair (or his designate) for consolidation and distribution to all DWG members for comment and/or additional revision. Depending on the magnitude and nature of the revisions being considered, this review process may require more than one cycle before approval is considered. The DWG Chair should give consideration to being able to complete the review and revision process in time to avoid any delays in collecting dynamic data or completing other DWG work.

The DWG Chair may seek approval of any revision, addition or deletion to the PROCEDURAL MANUAL by E-mail vote, regular meeting or called special meeting as deemed necessary or requested by DWG membership.

### FLAT START TUTORIAL

The flat start is performed by each DWG member on their data prior to submitting data to ESP. A member designated by DWG will perform a flat start on the complete ERCOT database. The outcome of a flat start will be simulation ready base case (the converted base case) with associated dynamic file (SNAP file, a PTI dynamic data file.)

The following steps are followed to perform the flat start. For more information refer to the PTI Program Application Guide Volume 2, Chapter 12.

Create a working directory for saving working files.

Copy the load flow case(s) to be studied to the working directory.

Copy the dynamics data base to the working directory. ESP compiles the dynamics database.

- Start  the PSS/E  DYNAMICS program by creating a link to PSSDS4 that starts at the working directory – edit ‘properties’ and set the ‘start in’ field - and execute the following activities until there are no errors:

- Activity LOFL

This activity is used to retrieve the load flow case. Select the ERCOT load flow case to be studied from the working directory

- Activity RDCH – to make network changes

- (usually performed by executing the network changes idv file)

- With this activity, network updates will be applied to the base case to match the dynamic data.

- Activity RDCH – to make zsorce changes

- (usually performed by executing the zsorce idv file)

- This activity will match the zsorce value in the base case to match the value provided in the dynamic data.

- Activity GEOL ALL

This activity will list machine terminal conditions. Check for MBASE of 0 and correct. GEOL checks machine reactive loading against an assumed capability curve.   This calculation uses MBASE. Units operating outside of their reactive limit will show up “overloaded” and the reactive output should be reviewed and corrected if necessary. This activity must be used for screening the data. .

- Activity FNSL OPT

This activity is used to solve the selected load flow case using the Full Newton-Raphson solution method. Modify load flow parameters if needed.

Activity GNET

(usually performed by executing a GNET idv file)

This activity converts a generator bus to a load bus for lack of dynamic models.

- Activity CONL

- (usually performed by executing a CONL idv file)

This activity converts constant MVA load to desired constant power, current, and admittance characteristics.

The three choices are:

1. Constant power – power remains constant, P= k

2. Constant current – power varies linearly with V, P= VI*

3. Constant admittance – power varies quadratically with V, P=V2*Y

- Activity CONG ALL

This activity converts all on-line generators (fixed power and voltage source) to a NORTON current source equivalent that is used by the DYNAMICS program.

- Activity ORDR

- Activity FACT

Factorizes admittance matrix for activity TYSL

- Activity TYSL

This activity is a triangularized Y matrix network solution used in dynamics studies. It cannot handle fixed power and voltage LOADFLOW generation representation. It produces very small mismatches (If TYSL takes more than two or three iterations to reach tolerance, make sure the original LOADFLOW solution was good) so that initial conditions are good for dynamics.

- Activity SAVE

This activity saves the converted load flow case to be used for dynamics study.

- Activity RTRN

Returns to DYNAMICS program

- Activity DYRE

This activity reads in the dynamics data file created by ESP.

Note and document any error messages. You will be asked for the ”CONEC’’, ‘’CONET”, and “COMPILE” file name.

Activity CHSB

This activity is similar to the activity CHAN except that it allows the user to select a subsystem for monitoring simulation variables.

- Activity CHAN

This activity selects the output channels to be stored during the dynamic simulation. Typically, ANGLE, PELECTRIC and ETERMINAL are selected. The bus number and machine number for each unit must be given for each output channel picked.

- Activity SNAP

###### This activity stores the data associated with the modeling of dynamic equipment.  Execute SNAP and save the dynamics data to a snap file.

- Activity STOP

If DYRE places no model calls in CONEC or CONET, you will get the following message:

“NO MODEL CALLS IN CONNECTION SUBROUTINES – DYNAMICS SKELETON MAY BE USED”.

Skip the COMPILE and CLOAD4 steps.

If DYRE placed any model calls in CONEC or CONET, you will be instructed to “COMPILE AND CLOAD4 BEFORE RUNNING SIMULATIONS” See following paragraphs for details.

From DOS, open the WORKING directory. To perform the next two steps, the computer system must include a FORTRAN compiler with all patches recommended by PTI.

From DOS and the working directory:

Execute COMPILE

Execute CLOAD4

If user-defined models are present, they should be included on the command lines, for them to be compiled and linked as well.

Execute COMPILE MyUserModel

Execute CLOAD4   MyUserModel

This compile command links the user model, CONEC and CONET to PSS/E by creating a file called "DSUSR.DLL", a dynamic link library used by PSSDS4.

To run a simulation, rerun PSSDS4’s link residing in the working directory.

PSSDS4 [enter]

PSSDS4 first looks for the file "DSUSR.DLL" that is located in the

working directory, needed when user model are included.  If the dll file is not there, it will use the default copy located in PSSLIB, which does not contain any user models.

Activity RSTR

Read in the snapshot file saved during setup.

##### Activity LOFL

- Activity CASE

Read in the converted case saved during setup.

- Activity ORDR

- Activity FACT

Activity TYSL

- Activity RTRN

- Activity ALTR

This activity changes the solution parameters (6) time step (DELT) to 0.004167 Seconds (¼ cycle). Note that some induction machines may have very small time constants requiring time steps of 0.000104 seconds (1/16 cycle).

- Activity STRT

This activity sets initial conditions and performs numerous data checks.

The number of errors may be too large so it is better to create an error file to save errors to. To do this:

- Activity OPEN  - Give file name to save errors

Activity PDEV

You must check all initial conditions reported by STRT carefully. The initial load-flow should converge in one iteration.  The listed DSTATE values should be within 3% to 5% of the corresponding state value.  Note that a state is a variable with a constant initial value. A DSTATE is a time derivative of the sate variable. Since there are no disturbances, DSTATE should be zero.

Also, upon completion, STRT instructs the user to enter the simulation output filename to be used by activity RUN in the dynamic simulation.  The user will also be asked to enter a snapshot filename to preserve the system initial conditions. No snapshot filename must be specified at this time.

- Activity RUN

This activity does the numerical integration of the differential equations (the simulation). You must enter a value for TPAUSE and NPLT. TPAUSE is the duration of the simulation. To test the simulation setup, run the simulation for 10 seconds. NPLT is the interval in # of time steps to write the simulation output to the channel file for plotting (NLPT should be an odd number).

# TPAUSE 	= 10

NPRT      	= 3

# NPLT 		= 1

CRTPLT	= 3

- Activity STOP

- When the simulation is over, this activity terminates execution of PSSDS4.

- PSSPLT

- This is the PSS/E plotting program.

- Activity CHNF

Enter name of simulation output channel file.

- Activity RANG

This activity scales the output channels. Choose option which generates common scale (X).

- Activity IDNT

This activity identifies the output channels. You must give it a range.  No identifier mask needs to be given.

- Activity SCAN

Choose option for maximum angle spread Option (3)

- Activity SLCT

This activity selects the output channels to be plotted once identified. The output channels are automatically scaled by the RANG activity but you should choose a scale that will be large enough for consistency and comparison purposes. Six channels may be plotted at a time.

- Activity PLOT

- This activity plots the output channels chosen. A title for the PLOT can be given.

- Activity STOP

You must get out of PSSPLT before any plots will be made. Once you are out, you are asked for the number of copies wanted and the name of the plotting device.

### Dynamics Working Group 2004 Roster

(at least one entry per ERCOT area as defined in the base case)

### Austin Energy				Reza Ebrahimian

### AEP	Vance Beauregard

### City Public Service Board			Michael Spence

GGTMPA                                                  Danh Huynh, David McCalla

### Center Point                                             Wes Woitt

### Lower Colorado River Authority		Tom Bao, Chair

### Public Utilities of Brownsville		James McCann

### South Texas Electric Cooperative		John Moore

### ONCOR				           Roy Boyer, Vice Chair

### TNMP						Anthony Hudson

ERCOT System Planning			Jose Conto, Juan Santos

ERCOT Operations                                  Yan Ou

PTI has authorized use of PTI information to be included in this Procedural Manual.

2 The reference to the DWG member that submit data is for the data owner as defined in section I.