## Slide 1
Alternative Fuel Survey Results
Technical Advisory Committee Meeting
December 2nd, 2004
Reliability and Operations Subcommittee Report
Presented by ERCOT Client Relations

## Slide 2
Survey Participants:
  Resource Entities - 104
  Generation Units - 550
Survey respondents:
  Resource Entities/Percentage - 93 / 89%
  Generation Units/Percentage - 517 / 94%
  MW represented by Respondents - 95% of ERCOT Total

## Slide 3
What is the Unit’s Primary Fuel Type?
Primary Fuel # of Units % of Units % of Output
Natural Gas 423 82% 75%
Lignite 12 2% 10%
Bituminous Coal 6 1% 4%
Sub Bituminous Coal 7 1% 4%
Nuclear 4 1% 4%
Wind 17 3% 1%
Purchased Steam 6 1% 1%
Water 30 6% 1%
Petroleum Coke 1 0% 0%
Landfill Gas 5 1% 0%
Distillate Fuel Oil 6 1% 0%
Out of the 517 total units represented by survey respondents

## Slide 4
Is the Unit capable of operating on an alternative fuel?
Dual Fuel Capability # of Units % of Units % of MW Capacity
Yes 148 29% 32%
No 369 71% 69%
All dual fuel capable units had Natural gas as the Primary Fuel

## Slide 5
What is the alternative fuel type?
Alternate Fuel # of Units % of Units % of MW Capacity
Distillate Fuel Oil 1 119 80% 84%
Residual Fuel Oil2 18 12% 12%
Other Gas3 5 2% 3%
Jet Fuel 2 1% 1%
Propane 4 3% 0%
Total 148
1 – Diesel, No 1 Fuel Oil, No 2 Fuel Oil, No 4 Fuel Oil
2 – No 5 Fuel Oil, No 6 Fuel Oil
3 – Butane, Coal Processes, Coke-oven Coal, Methanol, Refinery gas
Out of the 148 dual fuel capable units:

## Slide 6
What is the unit’s maximum net sustainable
limit when using its alternative fuel?
Alternate Fuel Registered Output Max. Net Sustainable Output
Distillate Fuel Oil 1 23,062 18,349
Residual Fuel Oil2 3,395 3,124
Other Gas3 757 710
Jet Fuel 164 150
Propane 80 77
Total 27,458 MW 22,410 MW
Out of the 148 dual fuel capable units:

## Slide 7
Does the unit have the needed infrastructure in place
for alternative fuel delivery, storage, and fuel management?
Infrastructure # of Units % of Units % of MW Capacity
Yes 145 98% 98%
No 3 2% 2%
Of the 148 dual fuel capable units:

## Slide 8
Is the dual fuel capacity currently operational?
Of the 148 dual fuel capable units:
Operational # of Units % of Units % of MW Capacity
Yes 119 80% 85%
No 29 20% 15%

## Slide 9
Can the unit operate on Automatic Generation Control (AGC)
when using its alternative fuel?
Of the 119 operational dual fuel capable units:
Operational on AGC # of Units % of Units % of MW Capacity
Yes 66 55% 77%
No 53 45% 23%

## Slide 10
Can the unit start up on its alternative fuel?
Of the 119 operational dual fuel capable units:
Start up # of Units % of Units % of MW Capacity
Yes 56 47% 31%
No 62 52% 68%

## Slide 11
Can the unit operate at maximum capacity using only its
alternative fuel or does it need a combination of primary
and alternative fuel?
Of the 119 operational dual fuel capable units:
Operation at 100% Capacity # of Units % of Units % MW Capacity
Alt. Fuel Only 72 61% 41%
Need Mixture 47 39% 59%

## Slide 12
If a combination of fuels is needed to operate the unit,
what is the percentage of alternative fuel needed to operate
at the unit’s maximum capacity?
Of the 47 operational dual fuel capable units that need a mixture:
Operation at 100% Capacity % Alternate Fuel needed at Max
Need Mixture 60%(Average)
Wide range of responses

## Slide 13
Do you regularly test the unit’s ability to operate on
its alternative fuel?
Of the 119 operational dual fuel capable units:
Regularly Tested # of Units % of Units % of MW Capacity
Yes 62 52% 55%
No 57 48% 45%

## Slide 14
If yes, how often do you test the unit’s ability to
operate on its alternative fuel?
Of the 62 operational dual fuel capable units that test regularly:
Testing Period # of Units % of Units % of MW Capacity
0-6 Months 16 26% 38%
7-12 Months 41 66% 44%
1-2 Years 5 8% 8%

## Slide 15
Do you maintain alternative fuel inventory?
Of the 119 operational dual fuel capable units:
Maintain Fuel Inventory # of Units % of Units % MW Capacity
Yes 112 94% 96%
No 7 6% 4%

## Slide 16
Do you currently have air emission permits to operate the
unit using the secondary fuel?
Of the 119 operational dual fuel capable units:
Air Permit # of Units % of Units % of MW Capacity
Yes 115 97% 98%
No 4 3% 2%

## Slide 17
How many hours in a rolling 12 month period can the unit
operate using its alternative fuel, at maximum sustainable
capacity, and complying with air emissions
limits?
52 of the 119 operational dual fuel capable units that responded to this question
Hours w/ Limits # of Units % of Units % of MW Capacity
0-101 - - -
101-200 1 1% 0%
201-300 3 3% 1%
301-400 - - -
401-500 - - -
500-1000 28 24% 18%
1001-2000 2 2% 1%
2001-5000 2 2% 1%
5000-8760 21 18% 7%

## Slide 18
How many hours in a rolling 12 month period can the
unit operate using its alternative fuel, at maximum
sustainable capacity and ignoring emissions limits?
75 of the 119 operational dual fuel capable units that responded to this question
Hours w/o Limits # of Units % of Units % of MW Capacity
0-101 32 27% 34%
101-200 1 1% 0%
201-300 1 1% 0%
301-400 1 1% 1%
401-500 - - -
500-1000 2 2% 2%
1001-2000 2 2% 1%
2001-5000 - - -
5000-8760 38 32% 18%

## Slide 19
How many hours can the unit operate
using your current inventory of alternative fuel,
at its maximum sustainable capacity?
Hours w/o Limits # of Units % of Units % of MW Capacity
0-10 2 2% 4%
11-20 7 6% 8%
21-30 2 2% 1%
31-40 8 7% 12%
41-50 8 7% 5%
51-100 51 43% 36%
101-200 26 22% 26%
201-300 1 1% 1%
301-400 3 3% 1%
401-500 - - -
501-1000 2 2% 1%
110 of the 119 operational dual fuel capable units that responded to this question

## Slide 20
Hours of Operation on current inventory

## Slide 21
Hours of Operation on current inventory

## Slide 22
If the unit's alternative fuel is oil, how many barrels of oil do you
currently maintain for all units at the plant as inventory?
Wide range of responses
Data will be presented to ROS and included in the final report

## Slide 23
How many hours does it take to switch fuels and operate
the unit using its alternative fuel at its maximum
sustainable limit?
Of the 119 operational dual fuel capable units:
Hours to Switch # of Units % of Units % of Output
0 6 5% 2%
1 46 39% 21%
2 19 16% 15%
3 8 7% 4%
4 15 13% 28%
6 12 10% 12%
8 6 5% 9%
12 3 3% 3%
15 2 2% 3%
24 1 1% 1%
48 1 1% 1%

## Slide 24
Questions?