## Slide 1: PRR525 SCE Method Comparison ERCOT Compliance December 3, 2004

## Slide 2: Why Meet Today?
Frequency control continues to be a concern
Non-regulating QSEs have no performance expectations that are measurable
URC Charges do not appear to be addressing frequency control issues

## Slide 3: PRR 525 Objectives
Apply measurement to non-regulating QSEs
  Concern exists that these QSEs don’t have anything to assess their relative performance
Consolidate regulation, balancing, and base schedule measures of performance
Minimize frequency swings during 0600 and 2200 ramp periods
  Tighten adherence to schedules
  Tighten adherence to Protocol-defined 10 minute ramp periods

## Slide 4
Method Similarities
1-minute & 10-minute measure
  Exclude intervals where a QSE’s generation is less than 1 MW.
  If Participation Factor < 1%, then 1% substituted
10-minute measure ONLY
  The absolute average SCE is compared to adjusted L10.
  |SCE| > adjusted L10 = Failed Interval
  Each QSE must pass 90% of the intervals per month.
  Scores are adjusted to exclude:
    OOMEs
    VDIs issued to all QSEs
    Portfolio & Resource Ramp Rate Violations.

## Slide 5: PRR 525 Method 10 Minute Measure
Participation Factor (PF) is the QSE’s actual generation divided by ERCOT’s total generation.
  Generation values are averaged in 10-minute intervals.
PF is included in the formula below to calculate adjusted L10.
  1.65 * 0.01315 * 6040 * 0.81 *

## Slide 6
PRR 525 Method 10 Minute Measure

## Slide 7
AEN Proposed Method 10 Minute Measure
Participation Factor (PF) is the QSE’s generation scheduled change divided by ERCOT’s total generation scheduled change.
  Generation scheduled changes are calculated in 15-minute intervals.
    These are averaged appropriately into 10-minute intervals.
  Generation Scheduled Change is defined as:
    Absolute Value [ (ResourceSchedule – ResourceSchedulePreviousInterval) + (BalancingDeployment – BalancingDeploymentPreviousInterval) ] + RegulationUpSchedule + RegulationDownSchedule
PF is limited to between 1% and 100%.
PF is included in the formula below to calculate adjusted L10.
  1.65 * 0.01315 * 6040 * 0.81 *

## Slide 8: AEN Proposed Detailed PF Calculation
IE
00
IE
15
IE
30
IE
45
IE
00
PF for this
Interval uses
data for IE 15
&
Previous IE 00
PF for this
Interval uses
data for IE 30
&
Previous IE 15
PF for this
Interval uses
data for IE 45
&
Previous IE 30
PF for this
Interval uses
data for IE 00
&
Previous IE 45
00 - 10
10 - 20
20 - 30
30 - 40
40 - 50
50 - 00

## Slide 9
AEN Proposed Method 10 Minute Measure

## Slide 10
Percent Obligation Method 10 Minute Measure
Adjusted L10 is 3% of the QSE’s obligation
  Min of 10 MW
  Max of 60 MW
Obligation is a QSE’s generation plus their Load Resource Response minus their SCE.
  This is averaged in 10-minute intervals.

## Slide 11
Percent Obligation Method 10 Minute Measure

## Slide 12
Method Comparison - October 10 Minute Measure

## Slide 13
Calculations are the same as what is currently done with Regulation Providers except for the participation factor.
  PRR525 Participation Factor is defined as:
    the QSE’s actual generation divided by ERCOT’s total generation. Generation values are averaged in 1-minute intervals.
  AEN Proposed Generation Change Participation Factor is defined as:
    the QSE’s generation scheduled change divided by ERCOT’s total generation scheduled change. Generation scheduled changes are calculated in 15-minute intervals. These are used for the 15 1-minute intervals in each 15-minute interval.
      See earlier slide for calculation.
SCPS1 Method Description 1 Minute Measure

## Slide 14
PRR525 SCPS1 Method 1 Minute Measure

## Slide 15
AEN Proposed SCPS1 Method 1 Minute Measure

## Slide 16
SCPS1 Method Comparison 1 Minute Measure

## Slide 17
Method Comparison
PRR 525 Method
  Gives extra SCE allowance to QSEs with a large amount of generation online.
  Easy to understand, tied to share of total ERCOT obligation in real time – regardless of AS obligations or BES deployments
  ERCOT must send participation factor signal that continually varies for QSEs to shadow measurement
AEN Proposed Generation Change Method
  Gives extra SCE allowance to QSEs with large schedule changes and provides extra allowance for regulation providers
  ERCOT must send participation factor signal that varies every 15 minutes for QSEs to shadow measurement
Percent Obligation Method
  Gives extra SCE allowance to QSEs with a large obligation.
  Simple, similar to BES performance criteria
  Easiest for QSEs to shadow – no participation factors

## Slide 18: 10-Minute Measure Statistics
October 2004
  30 QSEs evaluated
    10 QSEs failed all three measures
    4 QSEs failed the 525 but passed AEN & % OBL
    2 QSEs failed the 525 & AEN but passed % OBL
    1 QSE failed the 525 & % OBL but passed AEN
    13 QSEs passed all three measures
      Of these 13, 12 provided Regulation
  17 QSEs failed the 525 Method
  12 QSEs failed the AEN Method
  11 QSEs failed the % Obligation Method

## Slide 19: 1-Minute Measure Statistics
October 2004
  30 QSEs Evaluated
    3 QSEs failed 525 & AEN
    3 QSEs failed 525 but passed AEN
    2 QSEs failed AEN but passed 525
    22 QSEs passed 525 & AEN
  6 QSEs failed 525
  5 QSEs failed AEN

## Slide 20: Exclusions
Non-Spinning Ramp Periods (PRR 525)
Responsive Reserve Ramp Periods (PRR 525)
20 minutes after Unit Trip (Section 6.10.6)
VDIs issued to individual QSEs (Section 6.10.6)