## Slide 1
CenterPoint Proposed
Houston Area Constraint Mitigation Project
Information Presentation to TAC
January 6, 2005

## Slide 2
Presentation is for informational purposes only.
No determination or support is requested at this time.

## Slide 3
Loss of STP to Dow double circuit:
ckt
39 STP to WAP becomes the
limit with a 1413 MVA rating
X
South to Houston Thermal Constraint
Pre-contingency interface limit of approximately 2000 MW

## Slide 4
Loss of double circuit line
Jewett
to TH
Wharton
and
Gibbons Creek to O’Brien:
ckt
74
Jewett
to
Tomball
becomes
the limit with a 956 MVA rating
X
North to Houston Thermal Constraint
Pre-contingency
interface limit of
approximately
2400 MW

## Slide 5: CenterPoint Study Goals
Improve system reliability
Increase South to Houston transfer capability
  Thermal capability
  Voltage stability
Increase North to Houston transfer capability
  Thermal capability
  Voltage stability

## Slide 6
O’Brien
PHR
WAP
STP
Brazos
Valley
Oasis
Dow
Addicks
THW
Salem
Fayette Plant
Holman
Fayetteville
To San Antonio
To White Point
Option 27 with
Additional 345 kV
Improvements
Hillje
Upgrade
New

## Slide 7: CenterPoint Cost Estimate
Option 27 Estimated Cost
Thermal Upgrades Estimated Cost
Dynamic Reactive Additions
Estimated Cost
Total = $186 Million
$110 Million
$46 Million
$30 Million

## Slide 8: Study Calculated Transfer Capability Gains
Option 27 increases transfer capability from the South zone to the Houston zone by 2800 MW, corresponds to a S-H interface flow of approximately 3850 MW (1050 MW increase)
Option 27 increases transfer capability from the North zone to the Houston zone by 1000 MW, corresponds to a N-H interface flow of approximately 2900 MW (1900 MW increase)

## Slide 9: Status
Has completed South Regional Planning Group (stakeholder) presentation and review.
It is widely supported and no dissenting comments were received.
ERCOT Staff independent analysis is currently underway (includes economic impacts).
Many options are included as part of the review.
Expect to bring to TAC and BOD by April