## Slide 1: WMS UPDATE
PRR 525 Method Comparison
PRR 525 Method
  Gives extra SCE allowance to QSEs with a large amount of generation online.
  Easy to understand, tied to share of total ERCOT obligation in real time – regardless of AS obligations or BES deployments
  ERCOT must send participation factor signal that continually varies for QSEs to shadow measurement
AEN Proposed Generation Change Method
  Gives extra SCE allowance to QSEs with large schedule changes and provides extra allowance for regulation providers
  ERCOT must send participation factor signal that varies every 15 minutes for QSEs to shadow measurement
Percent Obligation Method
  Gives extra SCE allowance to QSEs with a large obligation.
  Simple, similar to BES performance criteria
  Easiest for QSEs to shadow – no participation factors

## Slide 2: WMS UPDATE
AEN Proposed Method 10 Minute Measure
Participation Factor (PF) is the QSE’s generation scheduled change divided by ERCOT’s total generation scheduled change.
  Generation scheduled changes are calculated in 15-minute intervals.
    These are averaged appropriately into 10-minute intervals.
  Generation Scheduled Change is defined as:
    Absolute Value [ (ResourceSchedule – ResourceSchedulePreviousInterval) + (BalancingDeployment – BalancingDeploymentPreviousInterval) ] + RegulationUpSchedule + RegulationDownSchedule
PF is limited to between 1% and 100%.

## Slide 3: WMS UPDATE
10-Minute Measure Statistics
October 2004
  30 QSEs evaluated
    10 QSEs failed all three measures
    4 QSEs failed the 525 but passed AEN & % OBL
    2 QSEs failed the 525 & AEN but passed % OBL
    1 QSE failed the 525 & % OBL but passed AEN
    13 QSEs passed all three measures
      Of these 13, 12 provided Regulation
  17 QSEs failed the 525 Method
  12 QSEs failed the AEN Method
  11 QSEs failed the % Obligation Method

## Slide 4: WMS UPDATE
  1-Minute Measure Statistics
October 2004
  30 QSEs Evaluated
    3 QSEs failed 525 & AEN
    3 QSEs failed 525 but passed AEN
    2 QSEs failed AEN but passed 525
    22 QSEs passed 525 & AEN
  6 QSEs failed 525
  5 QSEs failed AEN

## Slide 5: WMS UPDATE
PRR 527 A/S Performance
MOD Issues
Regulation and Responsive obligations in relation to OOME instructions
  Market Bulletin being issued to reinforce ERCOT notification
  Settlement is not affected
Non-Spin obligations in relation to OOMC instructions
  PRR is being issued to address the double payment issue
    Self-serve obligations will be problematic