## Slide 1: August 18, 2004 DCS Event
Loss of 1,115 MW of generation
Recovery time: 17:37 minutes
NERC DCS requirement – Recovery within 15 minutes
12 QSEs asked to explain SCE performance
  11 QSEs selected – Negative SCE 15 minutes following event (less than 95% of obligation)
  1 QSE selected – Negative SCE 10 minutes following RRS deployment (less than 95% of obligation)

## Slide 2: August 18, 2004 DCS Event Contributing Factors (Prior to Event)
ERCOT in process of ramping between intervals
Large schedule change in progress
QSEs’ scheduled more generation than the forecast
Large amount of down balancing was deployed

## Slide 3: August 18, 2004 DCS Event Contributing Factors (During the Event)
Faulty SCADA data
  ERCOT initially unaware of some unit trips
Additional generating unit trips
Poor governor performance
QSEs’ failure to understand & meet Protocols
Ramp rates not met – as stated in QSE Resource Plan
ERCOT did not declare an emergency & initiate the EECP

## Slide 4: Key Areas for Follow-Up Tracking and Reporting
Follow-up items
  ERCOT Operations
    Revise requirements for declaring EECP
    Develop procedures to deploy additional RRS if condition persists
    Review frequency control procedures including bias and RRS deployment / recall
  QSE Operations
    Communications with ERCOT
    Heightened sensitivity to SCE and Controls adjustments
    SCADA failures and corrective actions
    Increased understanding of Protocols
    Review scheduling practices by interval vs. hour

## Slide 5: Key Areas for Follow-Up Tracking and Reporting
Follow-up items (cont)
  Transmission Operator / TDSP
    Improve ability to isolate breaker testing
    Improve accuracy of field documentation
  Revise Protocol 6.10.5.4
    Include QSEs not providing RRS

## Slide 6: Disturbance Control Performance Adjustment
NERC Decision Pending
NERC Resources Subcommittee (RS) scheduled to meet on January 26th – 28th
Increase in Responsive Reserve Obligation proportional to the non-compliance with the DCS
Additional RRS carried for one calendar quarter
“Penalty” calculated to be 109 MW