## ERCOT Operations Report

## ROS & OWG

## January 2005

January Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 1/4/2005 6:08 | 59.897 | 26615 | -126 | 175 | 2590 (735) |
| 1/4/2005 23:01 | 60.135 | 27631 | -1119 | 438 | -1775 (-880) |
| 1/5/2005 0:28 | 60.103 | 24547 | -94 | 222 | 860 (860) |
| 1/6/2005 22:00 | 59.868 | 37590 | -197 | -625 | -3200 (-1315) |
| 1/8/2005 6:02 | 60.112 | 30747 | -293 | 752 | 2085 (1125) |
| 1/12/2005 23:00 | 60.110 | 27219 | -160 | 287 | -1425(-625) |
| 1/13/2005 5:13 | 60.138 | 25644 | 547 | 239 | 1300 (500) |
| 1/14/2005 5:51 | 60.142 | 34245 | -447 | 940 | 3600 (975) |
| 1/16/2005 13:59 | 60.166 | 30701 | -321 | 650 | -1275(-800) |
| 1/24/2005 13:07 | 59.855 | 31895 | 78 | -856 | VDI raise 500 MW. ERCOT experiencing control problems |
| 1/24/2005 13:35 | 60.145 | 31487 | -628 | -56 | VDI lower 500 MW. ERCOT experiencing control problems |
| 1/25/2005 8:22 | 59.890 | 33770 | 150 | -70 | Regulation not deploying as expected. |
| 1/25/2005 11:09 | 60.120 | 30805 | 33 | -8 | Regulation not deploying as expected. |
| 1/27/2005 5:36 | 60.109 | 26100 | -602 | 276 | Frequency >60.05 for 25 minutes |
| 1/27/2005 6:09 | 59.899 | 28547 | 163 | -389 | 3875 (825) |
| 1/28/2005 3:37 | 60.114 | 28074 | 92 | 135 | @03:33 ERCOT deploying 500 MW Up Reg in response to 1 QSE with an SCE of -545. At 03:37 the QSE's SCE = 110 and Up Reg was still recalling. |
| 1/28/2005 22:05 | 59.899 | 32297 | 122 | -393 | -2575 (-1390) |
| 1/31/2005 23:03 | 60.107 | 33337 | -401 | 220 | -1175 (-475) 589 MW Down Regulation recalled with no ramp. |

Disturbances

| 1/7/2005 12:54 | 59.849 | 560 |
| --- | --- | --- |
| 1/8/2005 21:00 | 59.880 | 450 |
| 1/9/2005 19:51 | 59.897 | 425 |
| 1/11/2005 0:32 | 59.899 | 330 (2 Unit/train) |
| 1/12/2005 13:28 | 59.871 | 460 (10 units ran back or tripped) |
| 1/16/2005 13:25 | 59.858 | 540 runback |
| 1/30/2005 10:40 | 59.847 | 545 |

Deployed Responsive (33) (Reported Above)

| 1/3/05 21:59:36 | 1/11/05 0:33:00 | 1/24/05 12:58:30 |
| --- | --- | --- |
| 1/4/05 6:07:48 | 1/12/05 13:28:08 | 1/25/05 6:03:36 |
| 1/6/05 3:10:16 | 1/13/05 6:11:10 | 1/25/05 8:14:12 |
| 1/6/05 21:59:08 | 1/14/05 12:33:16 | 1/26/05 12:44:10 |
| 1/7/05 12:54:06 | 1/15/05 12:18:26 | 1/27/05 6:02:40 |
| 1/8/05 0:02:16 | 1/16/05 13:25:20 | 1/28/05 2:19:40 |
| 1/8/05 21:00:08 | 1/19/05 1:16:54 | 1/28/05 22:05:06 |
| 1/9/05 11:01:36 | 1/21/05 6:25:44 | 1/30/05 10:40:38 |
| 1/9/05 19:51:32 | 1/21/05 22:05:18 | 1/30/05 21:59:00 |
| 1/10/05 0:00:56 | 1/24/05 6:03:24 | 1/31/05 6:01:40 |
| 1/11/05 0:01:52 | 1/24/05 10:47:54 | 1/31/05 22:00:06 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Jan 04 | Dec '04 | Jan 05 |
| --- | --- | --- | --- |
| DFW | 64 | 17 | 9 |
| E RIO | 41 | 47 | 9 |
| W RIO | 57 | 49 | 60 |
| Laredo | 43 | 43 | 44 |
| Bryan Area | 0 | 17 | 10 |
| Corpus | 31 | 38 | 31 |
| Abilene | 35 | 15 | 0 |
| San Angelo | 31 | 0 | 0 |
| Western | 7 | 14 | 0 |
| Houston | 4 | 0 | 4 |
| San Antonio | 0 | 1 | 0 |
|  | 313 | 242 | 167 |

OOME / Congestion Management Activity

| Contingency | Overload | Days |
| --- | --- | --- |
| Austrop - Sandow 345 kV | Austrop 345/138 kV Auto | 9 |
| North Edinburg - Bates 138 kV | Pharr Magic Valley - Polk Avenue | 6 |
| Big Brown - Venus 345 kV | Watermill - Cedar Hill Switch 345 kV | 4 |
| Eagle Pass - Asherton 138 kV | Uvalde - Asphalt 138 kV | 3 |
| Uvalde - Hamilton Road 138 kV | Asherton - West Conoco 138 kV | 3 |
| Bates - Frontera 138 kV | Pharr MVEC - Polk Avenue 138 kV | 3 |
| North Edinburg - Bates 138 kV | Pharr Magic Valley - Pharr 138 kV | 2 |
| Chamber - King & Cedar Bayou - North Belt | Cedar Bayou Auto AT2 | 2 |
| Fredericksburg - Gillespie 138 kV | Fredericksburg AT2 Auto | 2 |
| Heights - Freeway Park 138 kV | PH Robinson - Heights 138 kV | 2 |
| Holly - Airline 138 kV | Port Aransas - Mustang Island 69 kV | 2 |
| Rio Hondo 345 /138 Auto Transformer | Rio Hondo - La Palma 138 kV | 2 |
| Vernon-Lake Pauline 138 kV | Vernon-Chillicothe 69 kV | 2 |
| Austrop - Lost Pines 345 kV | Austop 345/138 kV Auto | 1 |
| Centerville Rd. - Forney Switch 345 kV | Seagoville AXFMR1L | 1 |
| Clear Spring - Marion - Zorn 345 kV | Loop 337 - Comal 138 kV | 1 |
| Dilley Switch - San Miguel 138 kV | Big Foot 138/69 kV Auto | 1 |
| Killeen Switch 345/138 kV Auto | Temple North - Temple Northwest 138 kV | 1 |
| Kingsville - Alice 138 kV | Falfurrias Auto | 1 |
| Laredo Plant - Falfurrias 138 kV | Derby Sub - Pearsall 69 kV | 1 |
| Menard 138/69 Auto | Mason - Fort Mason 69 kV | 1 |
| Military Highway AT1 | Military Highway AT2 | 1 |
| Monticello - Allen -Sulpher Spring 345 kV | Monticello - Paris Sw 345 kV | 1 |
| P.H. Robinson - Center 345 kV | Cedar Bayou Auto AT2 | 1 |
| Sargent Road to Watermill Switch 345 kV | Watermill Switch to Cedar Hill Switch 345 kV | 1 |
| Mt Enterprise - Trinidad/Martin Lake - Stryker Creek | Nacogdoches South East 345/138 kV Auto | 1 |
| Ennis SW - Monfort 138 kV | Waxahachie Pump 1 - MG Industries 138 kV | 1 |
|  | Ennis switch to Ennis West 138 kV | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

None

New Procedures/ Forms/ Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 01/20/2005 | ERCOT Power Operations Bulletin 145 | Procedure to Cancel OOMEs |
| 01/19/2005 | ERCOT Power Operations Bulletin 144 | Frequency Control Desk V3R14 - CN#169 |
| 01/19/2005 | ERCOT Power Operations Bulletin 143 | Frequency Control Desk V3R20 - CN#198 |
| 01/19/2005 | ERCOT Power Operations Bulletin 142 | Day Ahead Desk V3R17 |
| 01/19/2005 | ERCOT Power Operations Bulletin 141 | Frequency Control Desk V3R18 - CN#195 |
| 01/18/2005 | ERCOT Power Operations Bulletin 140 | Day Ahead Desk V3R17 |
| 01/18/2005 | ERCOT Power Operations Bulletin 139 | Day Ahead Desk V3R16 |
| 01/18/2005 | ERCOT Power Operations Bulletin 138 | Transmission & Security Desk V3R33 |
| 01/18/2005 | ERCOT Power Operations Bulletin 137 | Temporary Change - Frequency Control Desk CN#193 |
| 01/18/2005 | ERCOT Power Operations Bulletin 136 | Temporary Change - Frequency Control Desk CN#191 |
| 01/18/2005 | ERCOT Power Operations Bulletin 135 | Temporary Change - Operating Period Desk CN#192 |
| 01/13/2005 | ERCOT Power Operations Bulletin 134 | Transmission & Security Desk V3R30 |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems

1/12 13:38 High voltages on the 138 system in the McCamey area for a short duration following loss of two 138 line and multiple generation units.  One line tripped and reclosed and the second remained out of service due to damaged structures.  Ten units either ran back or tripped totaling 460 MW.  Most of these units were consuming a significant amount of MVAR and voltages of 1.09 pu were observed in the area for a few seconds following the unit trips.

Blackout/Load Shed incidences

None

# Communication

1/2 11:45    Held Interval.  SPD failed to solve for this interval.

1/16 03:45  Held 03:30 Interval.  SPD failed to solve for this interval.

1/24 12:30  Held 12:30 Interval until 13:30.  Deployments not being sent.

1/18   19:45-20:00 Balancing Energy market held.

1/24 12:30-13:30  Balancing Energy market held.

1/24   15:35-15:50 Portal not functioning.

1/25  	         Regulation not deploying as expected.  Adjusted gains in AGC at 17:00.

Major Computer Problems, Enhancements & Fixes

1/5 07:40   CAM trials commenced.

1/5 13:20   CAM trials terminated.

1/8 15:29   ERCOT opened a second A/S market.  A QSE submitted bids in error and could not provide the services.  Every award was doubled in the second market.  The doubling was observed on the portal but it is not known if the XML message reflected the doubled values.  The software problem has been turned in to EMMS and groundwork is being done on designs for a future enhancement.  In the interim, the problem is being corrected through procedure changes.

1/31 23:00	Recalled 589 MW of Down Regulation with no ramp.

ERCOT peak (Unofficial)

1/6/05		41,275

Update on New Generation

115 MW Wind farm in West Zone

90   MW Wind farm in West Zone

OCN, Advisory, Alert, Emergency Notice and Major Events

1/1 13:53  	Alert issued.  Insufficient Down Regulation.

1/5 10:12	Advisory issued.  Gas curtailments beginning 18:00\

1/5 18:00–22:00 OCN issued.  Capacity shortage due to projected fuel shortages.

1/5 22:00	Transmission Alert.  Loss of Uvalde – Hamilton loads Asherton – W Conoco.

1/6 00:00-10:00 Advisory issued for gas curtailments.

1/6 00:15 – 13:45 Transmission Alert.  Loss of Uvalde – Hamilton loads Asherton – W Conoco.

1/6 00:30-13:45 Transmission Alert.  Loss of Menard Try Loads Ft Mason – Mason.

1/7 02:00-04:15 Alert issued for capacity shortage 08:00 – 10:00.

1/10 06:30-08:30 Transmission Alert.  Apollo Tr 1 loading under multiple contingencies.

1/10  16:00-21:30  Transmission Alert.  Loss of Bates – Frontera loads Pharr MVEC – Polk Ave.

1/13  07:15-13:00/19:00-24:00  Transmission  Alert.  Loss of Uvalde – Hamilton loads Asherton –

W Conoco.

1/16  18:00-22:00   Transmission  Alert.  Loss of Uvalde – Hamilton loads Asherton – W Conoco.

1/16  19:00 	OCN issued.  Capacity shortage 1/17 08:00 – 10:00.

1/17  00:30	Alert issued.   Capacity shortage 08:00 – 10:00.  Alert cancelled at 08:00.

1/18  15:35-24:00	Transmission Alert.  Loss of Uvalde – Hamilton loads Asherton – W Conoco.

1/30  17:20-1/31 12:00  Transmission Alert.  Loss of Uvalde – Hamilton loads Asherton –

W Conoco.

1/30  16:30	OCN issued.  Insufficient Balancing bid for intervals 19:00-24:00.

1/31  12:00	OCN issued.  Insufficient Balancing bid for intervals 18:00-21:00 & 23:00.