## Slide 1
Transmission Services Update
South and West
Region Planning Group Meetings
ROS
February 10, 2004

## Slide 2: Meeting Agendas
West RPG (January 26)
McCamey Construction Status Report
2004 McCamey Study by ERCOT
Reactive Plan for McCamey
Dynamic Ratings for McCamey Lines
Potential use of SPS for McCamey Wind Generation
Upgrading Terminal Equipment to Meet or Exceed Conductor Ratings
5,000 MW and 10,000 MW Renewable Studies for TEPC and TREIA
South RPG (January 27)
MRA Implementation Process
Bates MRA RFP Update
Laredo MRA Technical Requirements
Potential MRA for Laredo
Houston Import Project Review Update
Both meetings held in Taylor with large turnout

## Slide 3: McCamey 2004 Top of Hour Production
Exceeds 500 MW
Exceeds 600 MW

## Slide 4: ERCOT WEST TEXAS
2003 -2005
Completed 2003
Completed 2002
Projected 2006
345 kV 345 kV with GIA 138 kV
Completed 2003
Completed 2003

## Slide 5: ERCOT West Texas Wind In-Service & Public Under Development
755 MW
75 MW
160 MW
41 MW
38 MW
150 MW
114 MW
225 MW
89 MW
175 MW
Total 1842 MW
(4352 MW with gas generation)
20 MW

## Slide 6: ERCOT West Texas Regional Constraint
REGIONAL CONSTRAINT
STABILITY LIMITED TRANSIENT & VOLTAGE
600 MW
1400 to 2000 MW
LOCAL CONSTRAINTS THERMAL & VOLTAGE

## Slide 7: ERCOT West Texas Constraint Projection
REGIONAL CONSTRAINT
STABILITY LIMITED TRANSIENT & VOLTAGE
600 MW
1400 to 2000 MW
LOCAL CONSTRAINTS THERMAL & VOLTAGE
NEW LOCAL CONSTRAINTS

## Slide 8: 2004 McCamey Study Conclusions
Large improvement with the 138 kV McCamey projects
  Transfer capability varies with fossil dispatch
  500-700 MW export capability when complete
  Voltage control problems observed above 600 MW generation export
345 kV lines were approved to be built when McCamey generation commits to 1,500 MW to 2,000 MW
  With additional improvements, projects increase the transfer capability from 760 MW to more than 2000 MW

## Slide 9: AEP Presentation on McCamey Transfer Limits
Tension monitors on limiting lines were installed by AEP
  Rio Pecos to Crane 138 kV
  North McCamey to Big Lake 138 kV
Proposal is to adjust line ratings dynamically in the McCamey area
  Wind drives both production and line ratings
Expected to provide significant increase in capacity
  Possible enough to meet all 755MW of installed wind resources
Any remaining line overload exposures may be handled with Special Protection Scheme(s)
Incorporation with operations is needed

## Slide 10: 5,000 MW Renewable Generation in West Region Rough Order of Magnitude Study for TEPC

## Slide 11: ERCOT West Texas Summary of Additions, 345kV Alternative
Total 5,000 MW
of Wind Projects
1900 MW
1500 MW
1600 MW

## Slide 12: 5000 MW Summary
 | McCamey | Morgan | Abilene | Total
Existing Gen | 750 MW | 250 | 200 | 1,200 MW
New Gen | 1,150 MW | 1,250 MW | 1,400 MW | 3,800 MW
Total | 1,900 MW | 1,500 MW | 1,600 MW | 5,000 MW
Total estimated cost of transmission upgrades is approximately $1 Billion
  Based on 345kV development option
  765kV option appeared higher in cost
TAC should consider an impact analysis of the integration of 5,000 MW of renewable generation in the ERCOT market

## Slide 13: South Region Planning Group Meeting

## Slide 14: South Region Planning Meeting
Must Run Alternatives (MRAs)
Review of the process for procuring MRAs and obtaining input from Stakeholders on the technical characteristics of MRAs
ERCOT will issue RFPs for MRAs in most instances
  Regional Planning Group (RPG) will have opportunity to comment to ERCOT on technical requirements
  RPG and TAC will have opportunity to comment to ERCOT on technical characteristics of short-listed proposals
ERCOT will be issuing a RFP for MRAs to the Laredo RMR contract
  Draft technical requirements to be included in the RFP presented
  Comments on technical requirements due 02/10/2005

## Slide 15: South Region Planning Meeting
Houston Import Project
The results of ERCOT’s independent economic analysis of the Houston Area Import Project was presented
  Two similar options were found to result in the most production cost savings relative to their cost
    Both options include the upgrade of the Jewett to Tomball / THWharton 345kV double circuit and a new 345kV circuit between STP and Parish
    The capital cost difference between the two options is about $20M
  Comments due to ERCOT by 02/04/2005 on qualitative factors
  ERCOT’s recommendation will be presented to TAC and the Board in March

## Slide 16: South Region Planning Meeting
Houston Import Project – 2 Preferred Options:

## Slide 17: South Region Planning Meeting
RMR Exit Status
AEP presented a status report on the transmission projects that must be completed in order for the Sempra RMR contracts to be exited
For more information, the presentations from the WRPG and SRPG meeting are posted at:
http://www.ercot.com/tmaps/

## Slide 18: Proposal to ROS for West Texas Dynamics WG Study
West Texas is dynamically limited for transfers out of the area
Additional detailed study with TO’s is needed to operating within limits
Request support from TAC ROS DWG to perform study using latest available models and data
Develop scope to be ready to implement

## Slide 19: Other Activity
NERC Review of ERCOT Planning Criteria
  Survey questions received 2/8/05 from NERC
  Will be forwarded to TO’s on Friday for return by 2/23/05 (short time frame)
  Presentation to NERC PC TIS March 1 (afternoon) in Houston (Sheraton IAH)