| OGRR Number | 161OGRR | OGRR Title | Responsive Reserve MW Limit |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | 2.5.2.3, Types of Responsive Reserve |  |
| Protocol Section Requiring Revision, if any. |  | ## N/A |  |
| Revision Description |  | Change the limit of RRS on an individual Generation Resource from 20% of Net Generation Capability to 20% of Net Generation Capability or 50MW, whichever is greater. |  |
| ###### Reason for Revision |  | The current limit is intended to ensure RRS is dispersed among enough Resources such that one or two Resources tripping off-line will not affect Responsive Reserve system reliability. Revising the limit to the greater of 50MW or 20% of the Net Generation Capability for any Resource would potentially increase participation and diversity in the Responsive Reserve market while still ensuring that no single Generation Resource carries too much of the total system Responsive Reserve. This revision is per a recommendation made in the 2004 Assessment of the Operation of the ERCOT Wholesale Electricity Markets, performed by Potomac Economics, LTD. |  |
| ###### OWG Recommendation |  | OWG recommends rejection of OGRR161. |  |

| Sponsor |  |
| --- | --- |
| Name | Scott Wardle |
| E-mail Address | Scott_Wardle@oxy.com |
| Company | Occidental Energy Ventures Corp. |
| Company Address | 5 Greenway Plaza, Suite 110, Houston Tx, 77046 |
| Phone Number | 713.215.7142 |
| Fax Number | 713.985.1453 |

Comments

This recommendation is based on:

1)	The Patton Review Task Force response to the Potomac Economics, LTD Whitepaper.

2)	ERCOT’s posted comments of 1/14/05 identifying system reliability concerns.

Proposed Operating Guide Language Revision

Note:  The Operating Guide baseline below includes OGRR149 which will be added to the Operating Guides upon implementation of PRR502

#### 2.5.2.3	Types Of Responsive Reserve

Reference:  Protocols Section 6.5.4, Responsive Reserve Service

Responsive Reserve Service (RRS) may be provided by:  (a) Unloaded Generation Resources that are On-line; (b) Resources controlled by high-set under-frequency relays; (c) Hydro Responsive Reserves; or (d) From DC Tie response that stops frequency decay.  The minimum amount of RRS provided by Generation Resources shall be as specified in the Operating Guides.  QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.  The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

Responsive reserves provided by a QSE shall meet the following requirements:

- (1)	In no case shall more than the greater of 50 MW or twenty percent (20%) of the Net Dependable Capability for any non-Combined Cycle thermal unit be used as Responsive Reserve.

- (2)	In no case shall more than the greater of 50 MW or twenty percent (20%) of the combined Net Dependable Capability for any Combined Cycle Block with one or more CTs or GTs coupled to a Steam Turbine, with their net maximum capability aggregated together, be used as Responsive Reserve.

- (3)	In no case shall more than the greater of 50 MW or twenty percent (20%) of the Net Dependable Capability for any hydro unit with a five percent (5%) droop setting operating as a generator be used as Responsive Reserve.