## ERCOT Operations Report

## ROS & OWG

## February 2005

February Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 2/3/2005 7:25 | 60.115 | 41071 | -1070 | 214 | SCE > 200 07:07-07:45. |
| 2/4/2005 3:50 | 60.111 | 30599 | -357 | 66 | VDI issued to reduce generation. Held interval after an incorrect OC1 limit was entered. |
| 2/4/2005 12:03 | 60.124 | 32940 | -305 | 289 | 515 MW of Down Regulation recalled with no ramp period, prompting Regulation providers to respond to negative SCE's. |
| 2/6/2005 1:32 | 60.103 | 24846 | -54 | 159 | 200 MW load reduction over previous minute |
| 2/6/2005 21:20 | 59.899 | 28315 | -156 | -525 |  |
| 2/11/2005 22:10 | 60.103 | 30293 | 264 | 163 | -2600 (-1025) |
| 2/11/2005 23:11 | 60.105 | 28369 | -214 | 76 | -1275 (-425) |
| 2/12/2005 22:07 | 60.101 | 27831 | 226 | 290 | -1950 (-575) |
| 2/13/2005 5:42 | 60.117 | 22625 | -77 | 150 | SCADA Frequency signal failed and defaulted to 59.868 during power interruption. RRS Deployed unnecessarily |
| 2/13/2005 18:40 | 59.767 | 30060 | 910 | -835 | 662 MW unit came off line over the hour and was not replaced.. |
| 2/14/2005 1:36 | 60.102 | 22163 | -67 | 275 |  |
| 2/14/2005 18:38 | 59.861 | 32722 | 910 | 23 |  |
| 2/14/2005 22:15 | 60.115 | 28401 | -117 | 144 | -4200 (-1000) |
| 2/17/2005 8:10 | 59.822 | 32422 | -162 | 257 | 630 MW unit trip |
| 2/17/2005 10:27 | 59.898 | 32315 | -676 | -515 |  |
| 2/19/2005 6:28 | 60.102 | 26595 | 272 | 412 |  |
| 2/20/2005 0:07 | 60.106 | 24387 | -21 | -22 | -2015 (-1240) |
| 2/20/2005 18:40 | 59.847 | 31161 | 910 | -1075 | 635 MW unit ramped down and tripped over HE 19:00 |
| 2/21/2005 6:52 | 59.897 | 28752 | -910 | -373 | 1110 (430) |
| 2/22/2005 22:38 | 60.129 | 28839 | -131 | 107 | AGC continued to request UP Regulation (+200) as frequency crossed 60 Hz. |
| 2/23/2005 1:25 | 59.843 | 23736 | 542 | -988 | 750 MW unit trip |
| 2/23/2005 3:22 | 60.105 | 22903 | -349 | 85 | 03:15 Interval Held. Hour ahead study results for IE 4 & 5 were suspect. |
| 2/24/2005 0:05 | 60.118 | 24901 | -445 | 409 |  |
| 2/24/2005 3:07 | 59.895 | 23979 | 33 | 836 | 1 QSE telemetered incorrect SCE of +966. Offset incorrectly calculated. 03:15 Interval Held. |

Deployed Responsive  (40) (Reported Above)

| 2/1/05 4:58:10 | 2/9/05 0:16:58 | 2/14/05 18:26:10 | 2/20/05 18:25:30 |
| --- | --- | --- | --- |
| 2/1/05 23:28:14 | 2/9/05 5:07:18 | 2/15/05 6:10:30 | 2/20/05 18:58:50 |
| 2/2/05 6:07:32 | 2/9/05 6:10:24 | 2/17/05 8:10:02 | 2/21/05 6:52:46 |
| 2/3/05 9:02:12 | 2/11/05 18:24:28 | 2/17/05 8:19:54 | 2/21/05 12:01:04 |
| 2/4/05 3:59:56 | 2/13/05 5:41:00 | 2/17/05 8:48:22 | 2/21/05 14:05:06 |
| 2/4/05 5:05:00 | 2/13/05 18:26:32 | 2/17/05 10:26:46 | 2/22/05 18:34:06 |
| 2/4/05 6:06:02 | 2/14/05 5:00:26 | 2/18/05 5:01:56 | 2/23/05 0:59:50 |
| 2/5/05 16:12:40 | 2/14/05 6:05:36 | 2/18/05 6:06:06 | 2/23/05 1:24:16 |
| 2/6/05 21:20:52 | 2/14/05 7:42:14 | 2/18/05 10:49:48 | 2/23/05 6:07:30 |
| 2/8/05 0:02:52 | 2/14/05 7:59:38 | 2/19/05 6:03:30 | 2/24/05 3:07:50 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Feb 04 | Jan 05 | Feb 05 |
| --- | --- | --- | --- |
| DFW | 58 | 9 | 8 |
| E RIO | 49 | 9 | 54 |
| W RIO | 58 | 60 | 29 |
| Laredo | 29 | 44 | 36 |
| Bryan Area | 0 | 10 | 13 |
| Corpus | 29 | 31 | 28 |
| Abilene | 36 | 0 | 0 |
| San Angelo | 27 | 0 | 0 |
| Western | 14 | 0 | 1 |
| Houston | 0 | 4 | 4 |
| Northeast | 0 | 0 | 7 |
|  | 300 | 167 | 180 |

OOME / Congestion Management Activity

| Contingency | Overload Element | # Occurrences |
| --- | --- | --- |
| North - West |  | 8 |
| Heights - Freeway Park 138kV | Heights - PH Robinson 138kV | 5 |
| Duke - Pharr Magic Valley 138 kV | McColl Rd - McAllen 138 kV | 4 |
| Royce Switch - Forney Switch 345kV | Seagoville Switch 345/138kV Auto | 4 |
| Vernon - Lake Pauline 138kV | Chillicothe - Vernon 69kV | 4 |
| Clear Spring-Marion-Zorn 345kV | Seguin to Seguin West 138kV | 3 |
| Killeen Auto 345/138kV | Temple Switch - Temple South East | 3 |
| South - North |  | 3 |
| Bates - Frontera 138kV | Frontera - North McAllen 138kV | 2 |
| Bates Unit 1 | Bates 138/69kV Auto | 2 |
| Big Lake-North McCamey 138kV | Fort Lancaster-Illinois #4 69kV | 2 |
| Centerville Rd. - Forney Switch 345kV | Seagoville Switch Auto 345/138kV | 2 |
| Chamber-King & CBY-North Belt 345kV | Cedar Bayou Auto CBYAT2 345/138kV | 2 |
| Dilley Sw - San Miguel Switch 138kv | Persall - Derby Sub 69kV | 2 |
| Dilly Sw - North Laredo 138kV | San Diego - Freer 69kV | 2 |
| Duke - Pharr Magic Valley 138kV | North McAllen - West McAllen 138kV | 2 |
| Gibbons Creek- Greens Prairie 138 kV | Dansby - Texas AM Sws 138 kV | 2 |
| Gibbons Creek-Twin Oak 345kV | Jewett-Watson Chapel 138kV | 2 |
| Graham - Sweetwater & Abilene Mulberry Creek 345kV | Graham - Murray TU 138kV | 2 |
| Holly - Airline 138kV | Port Aransas - Mustang Island 69Kv | 2 |
| Military Highway 138/69 T1 | Military Highway Transformer #2 | 2 |
| PH Robinson - Center 345kV | Cedar Bayou Auto CBYAT2 345/138kV | 2 |
| Westside to Barney Davis 138kV | Port Aransas - Mustang Island 69kV | 2 |
| North - Houston |  | 2 |
| Austrop - Lost Pines 345kV | Austrop Auto AT1H 345/138kV | 1 |
| Austrop - Sandow 345kV | Austrop Auto AT1H 345/138kV | 1 |
| Big Brown - Richland Chambers 345kV | Seagoville Switch 345/138kV Auto | 1 |
| Big Lake Xmfr W2 138/69kV | Fort Lancaster-Illinios 69kV | 1 |
| Cico - Pipe Creek 138kV | Cico to Comfort 138kV | 1 |
| Clear Spring-Marion-Zorn 345kV | Cico to Comfort 138kV | 1 |
| Clear Spring-Mrion-Zorn 345kV | Cico to Helotes 138kV | 1 |
| Comanche Peak-Decordova & Wolf Hollow-Rocky Rd | Spunky-Hood 138kV | 1 |
| Dupont - Whitepoint 138kv | Whitepoint - Rincon 138kv | 1 |
| Ennis West - Sterrett 138 | Desoto Sw - Red Oak 138kV | 1 |
| Friend Ranch - Big Lake 138kV | Ozona - Friend Ranch 69kV | 1 |
| Gibbons Creek - Twin Oaks 345kV | Boonville - Sutton 69kV | 1 |
| Gibbons Creek 345/138kV Auto | Jewett - Watson Chapel 138kV | 1 |
| LaPalma 345/138kV Auto | Rio Hondo - LaPalma 138kv | 1 |
| Monticello - Allen & Sulphur Springs 345kV | Monticello - Farmersville 345kV | 1 |
| North Edinburg - Bates 138kV | Polk Avenue - Pharr 138kV | 1 |
| North Edinburg - Rio Hondo 345kV | Magic Valley Weslaco - Weslaco 138kV | 1 |
| Noth Edinburg - Bates 138kV | Phar Mvec- Pharr 138kV | 1 |
| Sandow SES T1 345/138kV | Taylor - West Taylor 138kV | 1 |
| Temple-Lake Creek-Tradinghouse 345kV | Robertson-Milano 138kV | 1 |
| Uvalde - Hamilton 138kv | Asherton - W. Conoco 138kV | 1 |
| South - Houston |  | 1 |

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

RAP developed to protect temple Sw – Temple SE for the loss of the Killeen Tr.

New Procedures/ Forms/Operations Bulletins

| 02/08/2005 | Power Operations Bulletin 152 | Shift Sup. - New Appendix for Media Appeals for Voluntary Load Curtailments |
| --- | --- | --- |
| 02/11/2005 | Power Operations Bulletin 151 | DA Desk - Enhance Sections 2.9 and 2.10 for additional market opernings; Add hotline call to Section 2.18 step 5 |
| 02/08/2005 | Power Operations Bulletin 150 | T&S Desk - Update Appendix 8: Telephone Hotline |
| 02/08/2005 | Power Operations Bulletin 149 | T&S Desk - Issue an Advisory. |
| 02/04/2005 | Power Operations Bulletin 148 | FC Desk - Actions When Frequency Telemetry is Incorrect. |
| 02/02/2005 | Power Operations Bulletin 147 | OP Desk - Automated Offset Calculations. |
| 02/02/2005 | Power Operations Bulletin 146 | T&S Desk - Managing the Wind Powered Generation Resources in the McCamey Area |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems

None

Blackout/Load Shed incidences

2/10      06:00    138 kV line and approximately 18,000 customers lost due to weather.  All customers restored at

07:12.

# Communication

2/3	Held 23:45 interval.  RTB did not complete for 24:00.

2/4       Held 03:30 interval.  OC1 limit incorrectly entered.

2/17     Held 05:00 interval.  RTB did not complete for 05:15.

2/24      Held 03:15 interval.  Offset miscalculated.

Major Computer Problems, Enhancements & Fixes

2/24     AGC software patch installed to correct Regulation deployment problems.

ERCOT peak (Unofficial)

2/1 19:00	41,425

Update on New Generation

None

OCN, Advisory, Alert, Emergency Notice and Major Events

| 02-Feb-05 | 7:30 - 22:30 | Transmission Alert - Post contingency overload on Fort Mason - Mason 69kv with the loss of Menard Auto 138/69kv. |
| --- | --- | --- |
| 02-Feb-05 | 2:00 - 24:00 | Transmission Alert - Post contingency overload on Vernon - Chillicothe 69kv with the loss of Vernon - Lake Pauline 138kv |
| 03-Feb-05 | 08:30 - 23:00 | Transmission Alert - Post contingency overload on Fort Mason - Mason 69kv with the loss of Menard Auto 138/69kv |
| 03-Feb-05 | 0:15 - 3:00 & 8:30 - 24:00 | Transmission Alert - Post contingency overload on Vernon - Chillicothe 69kv with the loss of Vernon - Lake Pauline 138kv |
| 04-Feb-05 | 00:15 -12:34 | Transmission Alert - Post contingency overload on Vernon - Chillicothe 69kv with the loss of Vernon - Lake Pauline 138kv |
| 23-Feb-05 | 16:45-23:59 | Transmission Alert - Post contingency overload on Rio Hondo to La Palma for loss of La Palma Tr |