PV-BASED CONTINGENCY RANKING

ERCOT Independent Review of the              Houston Area Constraint Mitigation Project

ERCOT Transmission Services

March 2005

| Austin 7620 Metro Center Drive Austin, Texas 78744 Tel: (512) 225-7000 Fax: (512) 225-7020; www.ercot.com; Transmission Services - Taylor 2705 West Lake Drive Taylor, Texas 76574 Tel: (512) 248-6501 Fax: (512) 248-6560. |  |  |
| --- | --- | --- |

The Electric Reliability Council of Texas (ERCOT) Transmission Services staff prepared this document.  The use of this information in any manner constitutes an agreement to hold harmless and indemnify ERCOT, its Member Companies, employees, and/or representatives from all claims of any damages.  In no event shall ERCOT, its Member Companies, employees, and/or representatives be liable for actual, indirect, special or consequential damages in connection with the use of this data.

Table of Contents

Glossary										  3

Executive Summary								  4

History										  4

Proposed Project								  5

ERCOT Staff Independent Analysis						  6

First Stage									  6

Second Stage								  8

Third Stage							 	           12

Fourth Stage									15

ERCOT Staff Recommendation						20

Appendix A – Option Descriptions						22

Appendix B – Centerpoint Option 27 Details				24

Appendix C – Core Costs and Packages					25

Appendix D – Optimization Process						27

Appendix E – Final Options, Voltage Stability				32

Appendix F – Final Options, Transfer Analysis				34

Glossary

AEP – American Electric Power

ATC – Available Transfer Capacity

CM – Congestion Management

CNP – CenterPoint Energy

CSC -- Commercially Significant Constraint

Dow – Dow Substation

ERCOT – Electric Reliability Council of Texas

FCITC – First Contingency Incremental Transfer Capability

Hillje – Proposed CNP switching station

Jewett – Texas Utilities’ Jewett Substation

MUST – Shaw Power Technology software, “Managing and Utilizing System Transmission”

N-H  – North CM zone to Houston CM zone

NYMEX – New York Mercantile Exchange

OTDF – Outage Transfer Distribution Factor

PHR – CNP’s P. H. Robinson substation

PTDF – Power Transfer Distribution Factor

PMAX – Generating unit’s maximum generation capability

Powerworld – Powerworld Corporation’s Steady-State analysis software

pu – Per Unit Value

PV – Power versus Voltage relationship

RPG – Regional Planning Group

RMR – Reliability Must Run generating Units

S-H – South CM zone to Houston CM zone

SSWG – Steady State Working Group

STP – South Texas Project switching station

THW – CNP’s T. H. Wharton substation

Tomball – CNP’s Tomball substation

UPLAN – LCG Consulting’s market modeling software

VSAT – Powertech’s Voltage Security Assessment Tool, v4.2

Executive Summary

The Houston Area Constraint Mitigation project proposal was submitted by CNP in September of 2004 as a solution to congestion in the Houston area.  Stakeholder review of the project was favorable.  ERCOT determined that the project was economically driven rather than reliability driven as defined in the ERCOT Planning Charter.  Production cost modeling analysis was used to refine the CNP proposal and ultimately define the benefit it offered to the system.  ERCOT’s final recommendation was very similar to the CNP proposal.  The ERCOT-recommended project included upgrades to the Jewett to Tomball and Jewett to THW 345-kV corridors, the replacement or addition of four autotransformers in the Houston area, the construction of a new 345-kV switching station, construction of three new 345-kV lines in STP to WAP corridor, and several smaller upgrades.  According to CNP, the recommended changes could be complete as early as 2008.  The capital costs for the recommended option are estimated to be $121.9 million.  This equates to about $20.1 million in annual carrying costs.  Upon completion, this project will result in approximately $63 million in annual production cost savings and will increase the long-term reliability of the Houston area.

History

The Houston Area Constraint Mitigation project was created in response to economic congestion in the Houston area.  In recent years, large increases in the transfer from South Texas to Houston have been seen in actual ERCOT operations and in future ERCOT SSWG powerflow basecases.  The SSWG basecases use an economic generation dispatch that shows the South to Houston import far exceeding the system’s capabilities.  These transfers have resulted in the STP to Dow 345-kV corridor being designated as a CSC.  More than $37.4 million in balancing energy has been associated with this CSC since its inception in 2002.

In 2003, a new constraint appeared, limiting transfers into Houston from the north.  This new congestion resulted in the designation of a new CSC on the 345-kV corridor from Jewett to Tomball and Jewett to THW.  This CSC has resulted in $2.6 million in balancing energy charges in the first half of 2004 and continues to be a concern for ERCOT operations.

Most of the short lead-time upgrades to relieve congestion on these CSCs have already been exhausted.  In order to further increase the import capability into Houston and ensure future reliability, CNP prepared the “Houston Area Constraint Mitigation” proposal and submitted it to the South RPG in September 2004.   The proposal’s objective was to propose long-term upgrades that would relieve congestion to both of the Houston CSC constraints, increase reliability, and ensure the grid’s future ability to facilitate maintenance outages on those corridors.

During the subsequent RPG review and comment period (September/October 2004), market participant comments were mainly focused on differences in the use of line ratings for contingency loading as well as a discussion of the NERC planning criteria and its application in this proposal.  There was also a discussion concerning the need for a PHR – Oasis upgrade.  The comments did not include any opposition to the proposal.

Proposed Project

CNP began their evaluation with 27 options.  Descriptions of these options are listed in Appendix A.   Based on transfer analysis, voltage stability, and reactive support, CNP chose Option 27 and presented this as a project for the RPG and ERCOT to review.  This option is illustrated in Figure 1.  Details of this option can be found in Appendix B.

Figure 1 – CNP Option 27

ERCOT Staff Independent Analysis

ERCOT’s independent analysis was divided into four stages as illustrated in Figure 2.

Initial screening using CNP’s transfer analysis results

11 best perform- ing options

Economic optimization and grouping of each option

4 best perform-ing options

4-yr chronological production cost analysis

Final 2 options

Sensitivity

analysis and other factors

Recommendation

2nd Stage

3rd Stage

4th Stage

CNP’s initial 27 options

1st Stage

Figure 2 – Stages of Analysis

First Stage

The first stage of ERCOT’s review used the steady-state transfer results found in the CNP report to screen all of CNP’s 27 options.  This initial screening eliminated the options that were unlikely to perform as well as other options.  The remaining options underwent a more detailed economic analysis.  Even after screening, ERCOT’s economic analysis resulted in approximately 750 gigabytes of output data and over 500 hours of computer processing time.

The transfer results presented by CNP were based on the 2004 dataset B for summer peak in 2006.  Several changes were made to the ERCOT basecase.  The most significant included an infinite synchronous condenser in the Houston area, updated generator reactive capabilities, and modification of Dow and other Houston loads.

Four different dispatches were used in the CNP project proposal.  Starting with these dispatches, CNP used MUST to document the increase in FCITC transfer capability for all 27 proposed options.  The increases associated with each option were in addition to the FCITC transfer already present in the basecase.  The subregions used for the transfers were the 2003 ERCOT CM zones.  CNP used Rate A for contingency loading due to single-circuit outages and Rate B for contingency loading due to double-circuit outages.

Figure 3 shows the combined four dispatch average transfer increase (improvement above the basecase average FCITC) that results from the improvements found in each of the 27 options.

Figure 3 – Combined North to Houston and South to Houston Transfer Increases

Figure 3 illustrates that the different options have widely varying effects on the transfer capability into Houston.

The first ten options listed in Figure 3 (options 1, 4, 6, 7, 8 ,9, 11, 15, 17, and 18) provide significantly less transfer increase than the other options.  Therefore, these were removed from further consideration.  Option 16 requires 765-kV construction.  Because of the high capital cost and relatively small transfer increase, this option was dropped from consideration.  Options 3, 19, 20, 21, and 22, while providing large North to Houston transfer increases, provided little increase in the South to Houston transfer and were also removed from further consideration.

Eleven options were retained.  These options were moved into the second stage of the ERCOT review and are illustrated in Figure 4.  The graph represents the increase in FCITC above the value already in the basecase.  It should be noted that the results for Option 27 in both Figure 3 and Figure 4 do not include the new STP to Hillje line to be installed in the open position.

Figure 4 – Eleven Remaining Options

Second Stage

The second stage of the ERCOT analysis started by reviewing the capital costs associated with each of the eleven options.   These costs were categorized into two types.  Core costs were generally defined as 345-kV improvements that were unique to one or two of the options.  Supporting costs were generally considered to be 138-kV options that were common to most or all of the options.  Supporting costs were further divided into packages of related improvements.  In total there were eleven sets of core costs and eight packages of supporting costs.  Details for these packages can be found in Appendix C.

The eleven options were also categorized into five groups.  These groups were based either on similarities in their topologies or in the effect they had on the system.  The groups were used as a further means of screening the options.  Options within a group competed against each other with the goal of producing one winning option per group.  These groups are listed in Figure 5 and are illustrated in Figures 6 through 10.  Lines drawn in red represent new construction.

Figure 5 – Grouping of Options

Zenith 10

Zenith 14

Figure 6 – Zenith Options

West-12

West-13

Figure 7 – West Options

Parish 23

Parish 26

Figure 8 – Parish Options

Hillje 27

Hillje 25

Hillje 28

Figure 9 – Hillje Options

O’Brien 2

O’Brien 24

Figure 10 – O’Brien Options

After the options were put into groups, capital costs for the core projects and packages were collected.  This information was provided by transmission owners that would be the likely owners of the affected transmission elements.

Each of the eleven options went through a separate optimization process in which capital projects that were economically justified were included as part of the new optimized options.  Appendix D contains a detailed description of the process used to narrow the eleven options into four optimized options that are carried into the third stage of the analysis.    The final four options that emerge from the second stage of the analysis are listed in Figure 11.

Figure 11 – Final Four Options with Production Cost Savings and Capital Costs

Third Stage

The third stage of the analysis considered the four top-performing options from the third stage and modeled them over a four-year time frame from 2007 to 2010.  Consideration was given to when each part of each option was scheduled to be completed and the effect that completion had on each year’s production cost savings.

The annual production cost reductions for the years 2007 and 2008 were calculated using a 2008 basecase topology from the 2004 dataset B.  In 2009 and 2010, the production cost savings were based on a 2004 dataset B case for 2009.  Contingencies (including double circuits) were based on the ERCOT contingency file available on the ERCOT website.  Contingencies for new elements were also included when applicable.

The first step in this process was to determine the completion date for each of the transmission elements found in the optimized packages.  Estimated construction times were supplied by the same transmission owners that submitted the cost estimates.  These improvements and their expected in-service dates are listed in Figure 12.

Figure 12 – Construction Time Line

Using Figure 12 as a starting point, Figure 13 assumes that all the construction completed in a given year will be paid for in the previous year.   Capital costs for each improvement were escalated at 3% annually from the 2004 cost estimates.  These values are listed in Figure 13.

Figure 13 – Capital Costs

Similarly, production cost savings were calculated for each year from 2007 through 2010 as the improvements were completed.  Figure 14 contains the annual production cost savings for each option.  These savings represent the decrease in the overall production cost of the basecase when the option is included as a part of the system.

Figure 14 – Production Cost Savings

Figure 15 combines the annual capital costs in Figure 13 and production cost savings from Figure 14 into a single table in which the annual net cash flow is cumulatively added to the previous year.

Figure 15 – Cumulative Cash Flow

Figure 15 illustrates that both the Parish 26p1p3p4a and Hillje 27p1p3p4a have positive net cash flows before the end of 2009.  CNP’s original Option 27 is positive in 2010, while both Zenith10p1p2p4c and West12p1p2p3p4ad lag behind the other options and would have positive returns sometime after 2010.

Figure 16 graphically illustrates the results found in Figure 15.

Figure 16 – Cumulative Cash Flow

The options that have a positive net cash flow sooner are preferred because the certainty in the forecasted production cost savings decreases the further in the future those savings are found.  In contrast, the certainties of estimated capital costs do not vary inversely with time.  If anything, they have a tendency to be underestimated. Therefore, a project that recovers its capital costs more quickly would be preferred over a similar project that takes longer to recover its costs.

The conclusion drawn from that third stage of the analysis is that due to higher capital costs and less production costs savings, both Zenith10p1p2p4c and West12p1p2p3p4ad can be eliminated from further consideration.  Parish 26p1p3p4a and Hillje 27p1p3p4a are the top-performing options.  These optimized options, including all the packages, are illustrated in Figure 17.

Transmission elements illustrated in red indicate improvements or additions associated with each option.

Parish 26

Hillje 27

Figure 17 – Final Two Options

Fourth Stage

The final stage of the analysis examines the Hillje 27p1p3p4a and the Parish 26p1p3p4a options.  For the rest of this review these two options will be referred to as the Hillje 27 option and the Parish 26 option.

Both projects perform similarly and offer many of the same benefits.  It is therefore necessary to consider factors other than production cost analysis in examining these alternatives.  The fourth and final stage of the review includes voltage stability, transfer comparison, construction outages, maintenance outages, and production cost sensitivity to both natural gas prices and unit retirements.

ERCOT analyzed the voltage stability of both the final options using VSAT.  The final transfer limit for the two options was the same.  However, at transfer levels less than the collapse point, the Hillje 27 option provides slightly better voltage support.  Figure 18 illustrates this for the loss of the Jewett to THW and Jewett to Tomball 345-kV double circuit.  For both of the final options, this contingency was the most limiting in the single event contingency set.  A more complete discussion of the data and assumptions used in this study can be found in Appendix E.

Figure 18 – Voltage Stability

The original CNP report, as well as the first stage of this analysis, used the transfer capabilities of each option for screening purposes.   In this final comparison of the remaining two options, transfer improvements are revisited.

ERCOT used the 2005 dataset B for 2008 in this part of the analysis.  Figure 19 illustrates the increase in transfer capability over the basecase for each of the options.   The options vary little in transfer capability improvement.  Complete details for this part of the analysis can be found in Appendix F.

Figure 19 – Houston Transfer Improvement

ERCOT also considered the construction outages necessary to put both options into service.  The estimates listed in Figure 20 were provided by CNP, but should be considered preliminary.  Actual construction outages could vary for many reasons.

Figure 20 – Construction Outage Time

CNP’s estimates indicate that the construction of Hillje 27 instead of Parish 26 will require an additional ten to fifteen days of outages on 345-kV lines leaving STP.  Using production cost analysis, ERCOT modeled the cost for these outages during an off-peak period when one of the units at STP was out for refueling.  The combined cost for all five of the construction outages unique to Hillje 27 was less than $150,000. This indicates that the construction outage cost difference for the two options is not a significant factor in the overall decision.  See Figure 21.

Figure 21 – Construction Outage Costs

Maintenance outages should also be considered when evaluating the two options.  The Hillje 27 option is clearly the superior option for outage flexibility.  The new Hillje switching station, not present in Parish 26, effectively breaks the STP-Holman and WAP-STP lines into smaller segments resulting in shorter individual outages and lower congestion costs.

ERCOT examined the sensitivity of the forecasted production cost savings for the two options to changes in the market. The first sensitivity that was considered was the retirement of the Texas Genco units.  In January 2005 Texas Genco announced the retirement of eleven units totaling over 3800 MW of capacity in the Houston area.   The first three stages of this review where already complete at the time of the announcement, therefore consideration of the retirement was not included in those stages.

The Texas Genco units scheduled to be retired are all located in the Houston area.  This decrease in available generation makes both the final two transmission options more valuable from a production cost reduction standpoint.  Figure 22 shows these production cost savings in 2009 for the final two options.  The savings increase is greater for the Parish option than it is for the Hillje option, although both share similar results.  The Parish option outperforms the Hillje option for this sensitivity.

Figure 22 - Texas Genco Retirement Sensitivity

The final two options were also tested for sensitivity to changes in the natural gas forecast.  A new lower forecast, based on NYMEX future prices, was run in 2009 for both options.  Figure 23 shows the effect the lower gas forecast has on the production cost savings for both options.

Figure 23 – Natural Gas Price Forecast Sensitivity

Lower gas prices decrease the production cost savings for both options.   It should be noted, however, that even with the lower gas forecast both options remain viable and recover their capital costs in a two- to three-year time period.  The Parish option is less sensitive to the lower gas forecast resulting in a smaller reduction in production cost savings.  The Parish option outperforms the Hillje option for this sensitivity.

Figure 24 examines the combined effect of both a lower gas forecast and the possible retirement of the Texas Genco units.   In this scenario, both options are still viable – paying for themselves in a two to three year time period.  However, as in the other two sensitivities, the change in production cost benefit is greater with the Parish option.

Figure 24 – Combined Sensitivity

Finally, applying the same criteria used in the second stage of this analysis, the incremental improvements needed to transform the Parish 26 option into the Hillje 27 option return enough production cost savings to easily justify the inclusion of the improvements as a part of the preferred option.

Figure 25 summarizes the results for all the analysis done in the fourth stage of this review.

Figure 25 – Benefit Summary

ERCOT Recommendation

ERCOT recommends the Hillje 27 option be built.  This option increases the transfer capability into Houston while improving system reliability, operation flexibility and market efficiency.

The ERCOT recommendation includes the core costs associated with that Hillje 27 option along with packages 1, 3, and 4a.  This differs slightly from CNP’s initial recommendation.  These improvements will result in approximately $63 million a year in production cost savings upon their projected completion in 2008.  The overall capital costs for this project are estimated to be $121.9 million resulting in a carrying cost of $20.1 million annually.

Figure 26 lists the transmission improvements and the estimated capital costs included in ERCOT’s recommendation.

Figure 26 – Recommended Improvements

Appendix A – Option Descriptions

Option 1:  Build a new STP – Gibbons Creek 345-kV circuit.

Option 2:  Build a new STP – Gibbons Creek 345-kV circuit looped through O’Brien.

Option 3:  Build a new Crosby – Lufkin 345-kV double circuit.

Option 4:  Build a new Greens Bayou – White Oak 345-kV circuit.

Option 5:  Build a new Deepwater – Center 345-kV double circuit.

Option 6:  Build a new Oasis – HOC 345-kV double-circuit line along with a new HOC 345-kV substation containing two 345/138-kV autotransformers

Option 7:  Build a new Singleton substation at the Singleton corner and loop all circuits into the sub.

Option 8:  Singleton corner reconfiguration #1.  This option reconfigures the circuits at Singleton corner to produce a double-circuit line from Gibbons Creek to the Roans Prairie corridor and another double-circuit line from Jewett to the Zenith/THW corridor.

Option 9:  Singleton corner reconfiguration #2.  This option reconfigures the circuits at Singleton corner to produce a double-circuit line from Gibbons Creek to the Zenith/THW corridor and another double-circuit line from Jewett to the Roans Prairie corridor.

Option 10: Build a new Salem (LCRA) – Zenith 345-kV double-circuit line.

Option 11: Build a new Salem (LCRA) – Zenith corner 345-kV double-circuit line. This option is similar to Option 10 except that Zenith substation is not built, but instead the new double circuit is connected to circuit 99 Gibbons Creek to O’Brien.

Option 12: Build a new Fayette Power Plant (LCRA) – O’Brien 345-kV double-circuit line.

Option 13: Build a new Holman (Austin Energy) – O’Brien 345-kV double-circuit line.

Option 14: Build a new Zenith – Salem (LCRA) – TNP1 345-kV double-circuit line.

Option 15: Build a new 345-kV Hillje substation in STP corridor.  Loop circuit 39 STP – WAP and circuit 44 STP – Holman through the new sub.  Build a second Hillje to Holman 345-kV circuit.  Loop Lytton to Fayette 345-kV circuit through Holman.  Extend Fayette to Fayetteville 345-kV circuit to Salem.  Build new 345-kV double-circuit line from Salem to TNP1.

Option 16: Build a 765-kV circuit from Hillje to Singleton.  Build new 765/345-kV substations at Hillje corner and Singleton corner.  Loop all available 345-kV circuits into the substations.  Add two 1700-MVA 765/345-kV autotransformers at both locations.

Option 17: Replace limiting equipment on the two Jewett tie lines.

Option 18: Build Singleton substation and loop all 345-kV circuits into sub.  Upgrade both Jewett to Singleton circuits with higher capacity conductor and upgrade all equipment on the circuits to 3000 amps.

Option 19: Singleton corner reconfiguration #1.  Build Zenith 345-kV substation and loop all 345-kV circuits into the sub.  Upgrade Jewett to Zenith circuits with higher capacity conductor and upgrade all equipment on the circuits to 3000 amps.

Option 20: Upgrade the 345-kV corridors from Jewett to O’Brien and Zenith corner to THW with higher capacity conductor and upgrade all equipment on the circuits to 3000 amps.

Option 21: Build Singleton and Zenith 345-kV substations and loop all 345-kV circuits into the subs.  Upgrade Jewett to Singleton to Zenith circuits with higher capacity conductor and upgrade all equipment on the circuits to 3000 amps.

Option 22: Build Singleton and Zenith 345-kV substations and loop all 345-kV circuits into the subs.  Upgrade the existing Jewett to Singleton to Zenith circuits with higher capacity conductor and add two new high-capacity circuits from Jewett to Singleton to Zenith for a total of four circuits along the entire corridor.

Option 23: Build a new 345-kV circuit from STP to WAP.  Replace limiting equipment on the two Jewett tie lines.

Option 24: Build a new 345-kV circuit from STP to O’Brien.  Replace limiting equipment on the two Jewett tie lines.

Option 25: Build a new 345-kV substation at Hillje.  Loop in circuit 39 STP to WAP and circuit 44 STP to Holman into the new sub.  Build a second Hillje to WAP 345-kV circuit.  Upgrade both Hillje to WAP 345-kV circuits with higher capacity conductor and upgrade all equipment on the circuits to 3000 amps.  Replace limiting equipment on the two Jewett tie lines.

Option 26: Build a new 345-kV double-circuit line from Hillje corner to WAP and loop through circuit 44 STP to Holman, creating a second STP to WAP circuit and a Holman to WAP circuit.  Replace limiting equipment on the two Jewett tie lines.

Option 27: Build a new 345-kV substation at Hillje.  Build new 345-kV double-circuit line from Hillje to WAP.  Loop circuit 44 STP to Holman into new substation.  Replace limiting equipment on the two Jewett tie lines.  Add a third STP to Hillje circuit using the vacant tower position.

Option 28: Build a new 345-kV substation at Hillje.  Build new 345-kV double-circuit line from Hillje to WAP.  Loop circuit 44 STP to Holman and circuit 39 STP to WAP into new substation.  Add a third STP to Hillje circuit using the vacant tower position. Replace limiting equipment on the two Jewett tie lines.

(return)

Appendix B – CNP Option 27 Details

(return)

Appendix C – Core Costs and Packages

(return)

Appendix D – Optimization Process

Within each group individual options were optimized and compared to the alternatives in that same group.  The evaluation started with just the core projects of each option.  The optimization of the options was done by incrementally adding improvements to the core projects and then determining if that improvement was justified by comparing its capital costs to the reduction in the overall production cost of the entire system.  The end result was an optimal collection of improvements for each option that did not include any uneconomical improvements.  This stage of the analysis was done only for the year 2008.  It was assumed that all the improvements for each of the options could be in place by the beginning of 2008.  The Clear Springs – Salado project was not included in the case for this stage of the evaluation.  The Texas Genco units, recently designated for retirement, were considered available for dispatch.

Parish 26 will be used to detail the optimization process.  The core projects for the Parish 26 options had a capital cost of $80.1 million.  When those core projects are put in the case and evaluated for 2008, the overall production cost for serving the entire load in ERCOT is reduced by $32.3 million.  The ratio of capital costs to production cost savings is 2.48.  In Figure A, the core costs are in red, the production costs in blue, and their ratio in green.

Figure A

After the initial run with the core projects was made, the annual congestion report was examined.  In the case of Parish 26 one of the most heavily congested transmission elements was the Tomball 345/138-kV autotransformer.  Package 1 (Appendix C) upgrades this autotransformer and relieves this congestion.  It was added to the core projects associated with Parish 26.  The capital costs for package 1 were $7.5 million.  The addition of package 1 reduced the production cost savings by $12.5 million.  The new totals are illustrated in Figure B.

Figure B

The incremental addition of package 1 pays for itself in less than one year and is therefore considered an economically justified improvement.  Furthermore the addition results in the capital to production cost savings ratio decreasing from 2.48 to 1.96.  The optimized Parish 26 option now includes both the core projects and package 1.

Using the same process, the annual congestion report for the core cost plus package 1 run was examined, and the next most congested element that was included in the packages of supporting improvements was added to the case.  In this instance, the next package added was package 3, which included improvements in the Jewett to Tomball and Jewett to THW corridor.  The incremental impact of package 3 was a reduction in the production cost savings of $5.2 million.  Package 3 had a capital cost of $9.5 million.  Figure C illustrates this incremental change.

Figure C

Once again the incremental improvement offered by the package is economically justified.  The optimized Parish 26 option now includes the core costs and both package 1 and package 3.

Again, going back to the annual congestion report for the most recent results indicates that package 2, which upgrades the Lolita-Blessing-Lane City line, should now be looked at for congestion relief.  In this case, the addition of package 2 results in production cost savings of only $1.7 million at a capital cost of $32.1 million.  This indicates that package 2 is not an economically justified addition to the optimized option.  Therefore the optimal sets of improvements for Parish 26 remain the core costs, package 1, and package 3.  This is illustrated in Figure D.

Figure D

This process of incrementally adding packages and then evaluating their effect on production cost savings continues until all the packages are evaluated or there is no more congestion.  In the case of Parish 26 the optimal set of packages was the core costs, package 1, package 3, and package 4a.  This is illustrated in Figure E.

Optimal Set

Figure E

A similar analysis was done for each of the other options.  Figure F illustrates the first three sets of packages added to the core projects for Parish 23.

Figure F

The production cost savings and capital costs associated with Parish 23 were very similar to those found in Parish 26.  However, the actual construction of Parish 23 would require a costly outage of the STP-Parish 345-kV line that is not required with the Parish 26 option.  Therefore, at this point in the analysis it was decided to discontinue consideration of the Parish 23 option and to continue with the optimized Parish 26 option.

Each group of options was evaluated in a similar way in order to optimize each option and determine the winning option for each group.  Figure G illustrates the decision process for the West options.

Optimal Set

Figure G

The two West options were very similar.  Their main difference was the western termination point of the line.   The optimization showed that the West 12 option that terminates at the Fayette Plant was superior to the West 13 option.  It returned about 15% more in production cost savings while only costing approximately 5% more.  The West 12 option with package 1, package 2, package 3, package 4a, and package 4d was determined to be the winning option from this group.

Figure H illustrates the optimization used in the Zenith group.

Optimal Set

Figure H

The Zenith 14 option is clearly outperformed by the Zenith 10 option.  Zenith 14 is much more expensive and did not result in significantly more production cost savings.  The optimal Zenith option included the core cost for Zenith 10, package 1, package 2, and package 4c.

Figure I illustrates the optimization of the HIllje options.

Optimal Set

Figure I

All the Hillje options were very similar in both cost and performance.  However, construction of Hillje 25 would require a lengthy outage of the STP-Parish line that is not necessary for Hillje 27 and can therefore be eliminated from further consideration.  The Hillje 28 option returns slightly less production cost savings than Hillje 27 (after packages 1 and 3 are added) while costing slightly more.  Its construction would also require more outages than Hillje 27.  For these reasons Hillje 28 was also eliminated from further consideration.

O’Brien 24 clearly outperforms O’Brien 2.  The additional $105 million in capital costs needed to build a new line from O’Brien to Gibbons Creek results in only about $10 million in annual production cost savings.  In addition, the construction outage costs associated with O’Brien 2 would be very costly.  O’Brien 2 was eliminated from further consideration.

O’Brien 24 is very similar to the Parish 23 option.  The main difference is that the line from STP stops at Parish in the Parish 23 option, but in the O’Brien 24 option it bypasses Parish and stops at O’Brien.  This added distance causes O’Brien 24 to cost $36.4 million more than Parish 23.  It also requires a lengthy outage and actually returns less production cost savings.  Since Parish 23 was already eliminated from further consideration, O’Brien 24 will also not be considered for further analysis.

Both O’Brien options are eliminated from further consideration.  The O’Brien optimization is illustrated in Figure J.

Optimal Set

Figure J

(return)

APPENDIX E - Final Options, Voltage Stability

# Voltage Collapse Study Development and Process

PV simulations were performed the final two options as optimized by ERCOT and a 2009 basecase from the 2005 dataset B.  All the runs were done with Powertech’s VSAT v.4.2 software.  Basecases used in the analysis are listed in Figure A.  The total initial load in Houston CM zone was 18,772 MW.

Figure A – Basecases

The following contingency sets were screened for voltage collapse events:

Figure B – Contingency Sets

Some contingencies that result in voltage collapse, were identified as causing local collapse due to a radial network condition or an incomplete contingency definition.  These contingencies were excluded in the final runs.  Contingencies that resulted in voltage collapse far from the Houston area were also excluded from the final results.

Voltage-dependent loads replaced the static loads in the Houston area.  Load decomposition fractions were taken from VSAT data generated by Powertech for the 2003 ERCOT Voltage Security Study Phase II.  Percentages of total bus load were assigned to represent large motor, small motor, discharge lamps and constant power loads.  Houston loads without VSAT load data did retain their original constant power values.  Loads outside of Houston also retained their original static values.

All transmission buses 138-kV and above were monitored for under-voltage violations.  A bus was flagged for low voltage at 0.80 pu.

The load flow solution settings included turning the area control off to represent ERCOT as a single control area with a single swing bus.  Transformer taps were allowed to move in both pre and post-contingency conditions.  Switchable shunts were allowed to turn on or off.  Generator MW and MVar limits were enforced.  In some cases the export transfers were limited by generation capability.

The network was stressed with generator-to-load transfers.  With this process, power is incrementally transferred by increasing load in the Houston zone while increasing power from generators in zones outside of Houston.  Self-serve load in Houston was not scaled during the transfers.  At each new transfer increment, contingency sets were executed, followed by a load flow solution.  Voltage collapse scenarios were identified as those where the load flow solution did not converge.  The process was repeated for incrementally higher transfer levels until the case reached a point where either the pre-contingency basecase solution did not converge or the source zone generators reached their maximum capacity.

Study Limitations

This study was subject to the following limitations:

- Pre-existing conditions: The basecases contained overloads, voltage violations, n-1 violations and voltage collapse scenarios before any transfer was attempted.  Pre-existing conditions were not resolved prior to running this study.  The exception to this would be voltage collapse scenarios within the region under study that were either local or avoidable after appropriate network switching.

- Future network conditions: Neither maintenance nor forced outages were represented in this study.  Both conditions could affect the study outcome.

- Generation dispatch uncertainty.  The basecase was dispatched for minimum overloads on the ERCOT CSC interfaces, but there was no guaranty that such generation dispatch was the most severe to the region under study.  Furthermore, the generation capabilities modeled in the basecases, if different from what is available during actual operations, may have masked some voltage collapse events.

- Load modeling uncertainty: The truly voltage-dependent models and load fractions are unknown.  Load types (large motor, small motor, discharge lamp and constant power) were derived from accepted engineering practices starting from a load class dataset (proportion of residential, commercial and industrial customers at a load bus.)

- Under-voltage violations:  Depending on the composition of the load, low bus voltages could indicate the starting point for motor load stalling leading to fast voltage collapse.  Such conditions can be studied with full time-domain simulations, but were not included in the scope of this study.

Study Results

The study results are presented in tables for each basecase set and each contingency set tested.  The purpose of this analysis was to determine if either of the final two options had significant transfer capability above the other.  None was found. The optimized Options 26 and 27 both offered about the same level of transfer benefit over basecase transfers, when evaluated for voltage collapse.

PV margin was evaluated as follows (original zonal load for Houston = 18772 MW):

PV margin %=[ΔMW of Zonal Load][Original Zonal Load]x100%

# When subjected to the single event outage set, the Parish 26 option and the Hillje 27 option resulted in similar power transfer limits.  This limit exceeded the basecase limit by approximately 400 MW.  These results are illustrated in Figures C1, C2, and C3. Contingencies not listed produced PV margin bigger than 10%.

Figure C1 – Basecase Performance for Single Contingency Event

# Table C2 - Parish 26 Option performance to Single Event Outage Set

# Table C3 – Hillje 27 Option performance to Single Event Outage Set

# When subjected to the combined elements outage set, the Parish 26 option and the Hillje 27 option resulted in similar power transfer limits.  There was no improvement over the basecase limit.  These results are listed in Figures D1, D2, and D3. Contingencies not listed produced PV margin bigger than 5%.

Table D1 - Basecase performance to Combined Elements Outage Set

Table D2 – Parish 26 performance to Combined Elements Outage Set

Table D3 – Hillje 27 performance to Combined Elements Outage Set

(return)

APPENDIX F - Final Options, Transfer Analysis

Basecase Considerations

For this transfer analysis, the most recent 2005 dataset B basecase for 2008 was used.  This dataset was used in order capture the most up-to-date topology information.  The 2008 case corresponded with the earliest completion date projected for either of the final two options.

Three cases were used in ERCOT’s transfer analysis.  See Appendix C for full details about each option and associated packages.  The cases are described below:

- Base – This is the 2005 dataset B summer peak basecase for 2008.  The swing bus was moved from bus 49825 (WAP5) to bus 1703 (MOSES3).  A switched shunt in West Texas at bus 1064 (SUN) was set to fixed, since it would cause a divergent solution under certain conditions.

- Hillje – Basecase with optimized Option 27 implemented.  This includes Package 1, Package 3, and Package 4a.

- Parish – Basecase with optimized Option 26 implemented.  This includes Package 1, Package 3, and Package 4a.

Study Approach

The details of the transfer analysis were based on the following:

- The import region consisted of all generators online in the Houston CM Zone.

- The export regions consisted of the following:

- North – All online and offline generators in the North CM Zone

- South – All online and offline generators in the South CM Zone

- The basecase generation dispatch was used in the transfer study.  The only dispatch change made was adjustment of W.A. Parish Unit 5 to 90% of its PMax (90% of 646 MW).  This was done to balance generation at the new swing bus at Monticello Unit 3.

- The most recent ERCOT contingency file was used to calculate the FCITC of each transfer.  All new single and double contingencies associated with transmission additions in the Hillje and Parish cases were included when applicable.  Breaker-to-breaker contingencies, used by ERCOT operations, were also included in the analysis.

- PTI’s MUST software was used to make initial transfers between the import region and the two export regions.  The PTDF/OTDF sensitivity for reported transfer limits was set at 4%.  Many of the larger transfers reported by MUST had non-convergent solutions, so the MUST results were only used to screen for the worst contingency element for each transfer.

- Transfers studies between the import and export regions were modeled in Powerworld.  Using the worst contingency element found during the MUST screening studies, transfers were simulated and adjusted based on the worst limiting element for that contingency with a 4% or above OTDF.  Powerworld produced answers similar to those reported by MUST, but without the non-convergent solutions seen at high transfer levels.  The results reported in this report were taken from the PowerWorld program output.

Table A lists the results from the transfer study

Table 1:  Transfer Results

Table A – ERCOT Transfer Results

Conclusion

ERCOT’s review of the FCITC transfer level increase (improvement over basecase FCITC) attributed to each option was less than the amount found in the CNP’s analysis.   Overall FCITC values were somewhat higher.  Table B below was created using data from Table 3 in the original CNP report.

Table B - CenterPoint Energy Transfer Results

For Option 26 (Parish) and Option 27 (Hillje)

As seen in Figure 19 of the “ERCOT Independent Review of the Houston Area Constraint Mitigation Project”, the S-H transfer levels over the basecase in each Option are comparable to those observed by CNP.  The improvements to the lines from Jewett to Tomball and Jewett to T.H. Wharton allowed for slightly greater (~150 MW) transfers into the Houston area.  Improving these lines moves the “bottleneck” from the current N-H interface to the Temple/Killeen load center.  The implementation of the Clear Springs – Salado project may help to relieve this bottleneck, and increase transfers from North to Houston.

Differences in transfer capability can be attributed to a number of factors.  For example, transfers in the CNP cases were made in model year 2006, and transfers made in this analysis used model year 2008.  Also, the CNP cases were created from the 2004 SSWG dataset B and this analysis used the most recent cases in the 2005 SSWG dataset B.  There were also differences in rates used for contingency loading, as well as differences in the actual contingency lists.  A complete comparative analysis between the full CNP results and the results found here would help reveal more about the difference in transfer levels.

The purpose of this analysis was to determine if either of the final two options had significant transfer capability above the other.  None was found. The optimized Options 26 and 27 both offered about the same level of transfer benefit over basecase transfers.

(return)

Annual carrying cost based on 16.5% of total capital cost for project.

Based on a 3-year average nominal production cost savings (2008-2010) for Hillj27p1p3p4a listed in Figure 24.  Annual production cost for ERCOT is defined as the combined fuel, fixed, and variable costs required to supply energy needs of the ERCOT market for a given year.

CNP’s report, “Houston Area Constraint Mitigation Appendix A” contains a more complete description of the assumptions and processes used in attaining these results.

See second paragraph page 18 of CNP’s “Houston Congestion Relief Project”

Estimated construction outage cost is .1% of the project capital cost.

The Texas Genco announcement occurred after this portion of the analysis was complete.  In the UPLAN model for 2008, the Texas Genco retirement units generated .02% of the total ERCOT energy in the basecase.  After Hillje 27 was put in place that percentage dropped to .007% (approximately a 2/3 drop) of the ERCOT total energy needed in 2008.