| Date: | March 8, 2005 |
| --- | --- |
| To: | ERCOT Board of Directors |
| From: | Bill Bojorquez, Sam Jones |
| Subject: | ###### Houston Area Constraint Mitigation Project |

## Issue for the ERCOT Board of Directors

ERCOT Board of Director Meeting Date: March 15, 2005 Agenda Item No.: 6a

##### Issue: ERCOT Board endorsement of the Houston Area Constraint Mitigation Project.

##### Background/History: In recent years, large increases in the transfer of energy from South Texas to Houston have occurred in ERCOT operations and in ERCOT powerflow forecasts. As a result, ERCOT designated the STP to Dow 345-kV transmission line corridor and the 345-kV corridor from Jewett to Tomball and Jewett to the T. H. Wharton substation as Commercially Significant Constraints (“CSCs”). The short lead-time upgrades to relieve congestion on these CSCs have already been exhausted. CenterPoint Energy (“CenterPoint”) submitted the Houston Area Constraint Mitigation Project proposal in September 2004 as a solution to economic congestion in the Houston area. The proposal’s objective is to construct long-term upgrades that would relieve congestion on both of the Houston CSCs, increase reliability, and ensure the grid’s future ability to facilitate maintenance outages on those corridors. The South Regional Planning Group review of CenterPoint’s proposal resulted in several favorable responses to the project. ERCOT received no comments in opposition to the project. In January 2005, ERCOT Staff completed an independent review of the proposal. ERCOT Staff presented the review process and findings to the South Regional Planning Group for comment on January 27, 2005. ERCOT Staff’s recommendation included several changes to CenterPoint’s initial proposal, and it included two “best performing options” for final stakeholder review and consideration. All stakeholders who submitted comments supported ERCOT Staff’s final recommendation of the Hilje option. ERCOT received no comments in opposition to the revised project. When TAC considered the project at its March 3, 2005, meeting, TAC voted to recommend endorsement of the project – with one abstention and no votes opposed. According to CenterPoint, the recommended changes could be completed as early as 2008. The most significant planned improvements are shown below: A report detailing ERCOT’s evaluation of the Houston Area Constraint Mitigation Project is attached (Attachment A).

##### Key Factors Influencing Issue: CenterPoint estimates costs of the capital improvements needed to build the Houston Area Mitigation Project at $121.9 million (resulting in an annual carrying cost of approximately $20.1 million). ERCOT estimates annual production cost savings resulting from the completion of the project at $63 million per year. The project will provide much needed operational flexibility for maintenance outages of 345-kV lines tying the Houston area to the rest of the ERCOT grid. The project will also increase reliability for the Houston area from both a thermal and voltage standpoint.

##### Alternatives: (1) Endorse the need for the construction of the Houston Area Constraint Mitigation Project as recommended ERCOT Staff and TAC; or (2) remand to ERCOT Staff with instructions.

##### Conclusion/Recommendation: ERCOT Staff and TAC recommend the Board endorse the need for the Houston Area Constraint Mitigation Project as presented herein.