# SPWG Report to ROS

#### December 15th, 2004

The SPWG met November 18 and 19, 2004, in Houston, Texas.

SPWG members confirmed Mehrdad Vatani as the 2005 Chair and nominated Stan Ginsburg as the 2005 Vice Chair and request approval by ROS when appropriate.

By December 31, 2004, SPWG member companies to complete the loadability evaluation of zone 3 relays on lines rated 230 kV and above, in accordance with NERC recommendation 8a, using the winter 4 hour emergency ampere rating in the evaluation. Members to identify relays that do not meet the criteria and either a) file a request for exemption with ERCOT compliance or b) provide a plan to modify or replace relays that do not meet the criteria.

Current year (2005) short circuit case data is due to ERCOT by January 14, 2005.

SPWG members endorsed proposed changes to the SPWG Procedures. The modified document was submitted to ROS members for consideration.

Disturbance monitoring equipment location criteria presently applies to equipment operated at 60 kV or above. This is a change from wording previously approved by the SPWG specifying 100 kV and above. SPWG members agree reference to 60 kV should be revised to 100 kV. An OGGR will be prepared to address this issue, as well as time synchronization of disturbance recorders.

The next SPWG meeting is scheduled for February 24 and 25, 2005, in Fort Worth.

Jack Dahnke

SPWG Chair