## Slide 1
Alternative Fuel Survey Results
Reliability and Operations Subcommittee Report
December 15th, 2004
Presented by ERCOT Client Relations

## Slide 2
Basics:
Surveys received as of: December 14, 2004
Data as provided in the survey.

## Slide 3
Survey Participants:
  Resource Entities - 104
  Generation Units - 550
Survey respondents:
  Resource Entities/Percentage - 97 / 93.2%
  Generation Units/Percentage - 532 / 96.7%
  MW represented by Respondents - 97.2% of ERCOT Total

## Slide 4
What is the Unit’s Primary Fuel Type?
Primary Fuel # of Units % of Units % MW Capacity
Natural Gas 435 82% 75%
Lignite 14 3% 10%
Bituminous Coal 6 1% 4%
Sub Bituminous Coal 7 1% 4%
Nuclear 4 1% 4%
Wind 17 3% 1%
Purchased Steam 6 1% 1%
Water 30 6% 1%
Petroleum Coke 1 0% 0%
Landfill Gas 5 1% 0%
Distillate Fuel Oil 6 1% 0%
Out of the 532 total units represented by survey respondents

## Slide 5
Is the Unit capable of operating on an alternative fuel?
Dual Fuel Capability # of Units % of Units % MW Capacity
Yes 150 28% 31%
No 382 72% 69%
Of all registered units in ERCOT:
All dual fuel capable units (except 1) had Natural gas as the Primary Fuel

## Slide 6
What is the alternative fuel type?
Of the dual fuel capable units:
Alternate Fuel # of Units % of Units % MW Capacity
Distillate Fuel Oil 1 119 79% 85%
Residual Fuel Oil2 18 12% 11%
Other Gas3 5 3% 3%
Jet Fuel 2 1% 1%
Propane 4 3% 0%
Natural Gas 2 1% 1%
1 – Diesel, No 1 Fuel Oil, No 2 Fuel Oil, No 4 Fuel Oil
2 – No 5 Fuel Oil, No 6 Fuel Oil
3 – Butane, Coal Processes, Coke-oven Coal, Methanol, Refinery gas

## Slide 7
What is the unit’s maximum net sustainable
limit when using its alternative fuel?
Alternate Fuel Registered Output Max. Net Sustainable Output
Distillate Fuel Oil 1 23,502 18,674
Residual Fuel Oil2 2,955 3,124
Other Gas3 757 710
Jet Fuel 164 150
Propane 80 77
Natural Gas 320 305
Total 27,777 MW 23,040 MW
Of the 150 dual fuel capable units:

## Slide 8
Does the unit have the needed infrastructure in place
for alternative fuel delivery, storage, and fuel management?
Infrastructure # of Units % of Units % MW Capacity
Yes 147 98% 98%
No 3 2% 2%
Of the 150 dual fuel capable units:

## Slide 9
Is the dual fuel capacity currently operational?
Of the 150 dual fuel capable units:
Operational # of Units % of Units % MW Capacity
Yes 121 81% 85%
No 29 19% 15%

## Slide 10
Can the unit operate on Automatic Generation Control (AGC)
when using its alternative fuel?
Of the 121 operational dual fuel capable units:
Operational on AGC # of Units % of Units % MW Capacity
Yes 66 55% 74%
No 55 45% 26%

## Slide 11
Can the unit start up on its alternative fuel?
Of the 121 operational dual fuel capable units:
Start up # of Units % of Units % MW Capacity
Yes 58 48% 31%
No 62 51% 67%
No Answer 1 1% 1%

## Slide 12
Can the unit operate at maximum capacity using only its
alternative fuel or does it need a combination of primary
and alternative fuel?
Of the 121 operational dual fuel capable units:
Operation at 100% Capacity # of Units % of Units % MW Capacity
Alt. Fuel Only 72 60% 39%
Need Mixture 47 39% 59%
Optional (Alt Fuel only or Mix) 2 2% 2%

## Slide 13
If a combination of fuels is needed to operate the unit,
what is the percentage of alternative fuel needed to operate
at the unit’s maximum capacity?
Of the 47 operational dual fuel capable units that need a mixture:
Operation at 100% Capacity % Alternate Fuel needed at Max
Need Mixture 60%

## Slide 14
Do you regularly test the unit’s ability to operate on
its alternative fuel?
Of the 121 operational dual fuel capable units:
Regularly Tested # of Units % of Units % MW Capacity
Yes 62 51% 53%
No 59 49% 47%

## Slide 15
If yes, how often do you test the unit’s ability to
operate on its alternative fuel?
Of the 62 operational dual fuel capable units that test regularly:
Testing Period # of Units % of Units % MW Capacity
0-6 Months 16 26% 38%
7-12 Months 41 66% 54%
1-2 Years 5 8% 8%

## Slide 16
Do you maintain alternative fuel inventory?
Of the 121 operational dual fuel capable units:
Maintain Fuel Inventory # of Units % of Units % MW Capacity
Yes 114 94% 96%
No 7 6% 4%

## Slide 17
Do you currently have air emission permits to operate the
unit using the secondary fuel?
Of the 121 operational dual fuel capable units:
Air Permit # of Units % of Units % MW Capacity
Yes 117 97% 98%
No 4 3% 2%

## Slide 18
How many hours in a rolling 12 month period can the unit
operate using its alternative fuel, at maximum sustainable
capacity, and complying with air emissions
limits?
Of the 57 operational dual fuel capable units that responded:
Hours w/ Limits # of Units % of Units % MW Capacity
0-101 - - -
101-200 1 2% 1%
201-300 3 5% 5%
301-400 - - -
401-500 - - -
500-1000 28 49% 59%
1001-2000 2 4% 3%
2001-5000 2 4% 3%
5000-8760 21 37% 30%

## Slide 19
How many hours in a rolling 12 month period can the
unit operate using its alternative fuel, at maximum
sustainable capacity and ignoring emissions limits?
Of the 77 operational dual fuel capable units that responded:
Hours w/o Limits # of Units % of Units % MW Capacity
0-100 32 42% 58%
101-200 1 1% 0%
201-300 1 1% 0%
301-400 1 1% 1%
401-500 - - -
500-1000 2 3% 3%
1001-2000 - - -
2001-5000 - - -
5000-8760 40 52% 37%

## Slide 20
How many hours can the unit operate
using your current inventory of alternative fuel,
at its maximum sustainable capacity?
Hours w/o Limits # of Units % of Units % MW Capacity
0-10 2 2% 4%
11-20 7 6% 8%
21-30 2 2% 1%
31-40 8 7% 13%
41-50 8 7% 5%
51-100 51 46% 37%
101-200 26 24% 27%
201-300 1 1% 1%
301-400 3 3% 3%
401-500 - - -
501-1000 2 2% 2%
Of the 84 operational dual fuel capable units that responded:

## Slide 21
Hours of Operation on current inventory

## Slide 22
Hours of Operation on current inventory

## Slide 23
If the unit's alternative fuel is oil, how many barrels of
oil do you currently maintain for all units at the plant
as inventory?
Of the 80 operational dual fuel capable units that reported inventory:
Ranges of Inventory # of Units Total Barrels Percent of Inventory
200-500K 1 210,000 7%
100-200K 4 447,238 14%
60-100K 16 1,228,825 39%
20-60K 22 843,824 27%
10-20K 23 314,532 10%
0-10K 14 84,616 3%
TOTAL 80 3,129,035 100%

## Slide 24
How many hours does it take to switch fuels and operate
the unit using its alternative fuel at its maximum
sustainable limit?
Of the 121 operational dual fuel capable units:
Hours to Switch # of Units % of Units % MW Capacity
0 6 5% 2%
1 46 38% 21%
2 21 17% 16%
3 8 7% 6%
4 15 12% 27%
6 12 10% 12%
8 6 5% 9%
12 3 2% 3%
15 2 2% 3%
24 1 1% 1%
48 1 1% 1%

## Slide 25
Questions?