| OGRR Number | 159OGRR | OGRR Title | Clarification of QSE Schedule Control Error equation Bias Setting and Turbine Speed Governors |
| --- | --- | --- | --- |
| Recommended Action |  | Approve |  |
| Operating Guide Section Requiring Revision |  | 2.2.3.1 Bias Settings and 2.2.5 Turbine Speed Governors |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Proposed Effective Date |  | April 1, 2005 |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Clarification of QSE Schedule Control Error equation Bias Setting and reference to Protocol Section 5.8.2. Define Governor dead band per NERC Policy 1 and governor free to respond to all frequency deviations. |  |
| ###### Reason for Revision |  | Clarification of QSE Schedule Control Error equation Bias Setting and reference to Protocol Section 5.8.2. Define Governor dead band per NERC Policy 1 and governor free to respond to all frequency deviations. |  |
| OWG Recommendation |  | OWG recommends approval of OGRR159 as revised by OWG. |  |
| ROS Recommendation |  | ROS recommends approval of OGRR159 as recommended by OWG. |  |

| Sponsor |  |
| --- | --- |
| Name | Sydney L. Niemeyer PDCWG Chair |
| E-mail Address | sydney_l_Niemeyer@txgenco.com |
| Company | Texas Genco, LP |
| Company Address | 1111 Louisiana, Houston, TX 77002 |
| Phone Number | 713-207-5051 |
| Fax Number | 713-207-2145 |

Proposed Operating Guide Language Revision

#### 2.2.3.1	Bias Settings

In the Schedule Control Error equation,  QSEs shall have bias settings that approximate the measured frequency response characteristic of their On-line Resources.  This bias setting should be changed when significant On-line generating capability changes or when their Resources’ frequency response characteristics change.  The ERCOT Control Area Authority will check the area frequency response characteristic each time a disturbance qualifies as a measurable event per Section 5.8.2 of the Protocols.  Information thus obtained will be used to evaluate ERCOT and QSE bias settings.

### 2.2.5	Turbine Speed Governors

All governors must be placed in-service.

Governor performance tests should be conducted at least every two years and results used in analysis as described in Section 6.2.1, Turbine Governor Speed Regulation Tests.  A sample of such tests may be found in Section 6.2.1.2, Example of a Turbine Governor Speed Regulation Test for Mechanical Hydraulic Governor.  Every effort should be made to maintain governors with a five percent (5%) droop characteristic.

There are other elements that can contribute to poor governor response.  These include:

- Governor dead band.  Maximum intentional dead band: +/- 0.036 Hz.

- Valve position limits

- Blocked governor operation

- Control mode

- Adjustable rates or limits

- Boiler/turbine coordinated control or set point control action

- Automated “reset” or similar control action of the turbine’s MW set point.

Every attempt should be made to minimize the effects of these elements on the governor operation for the duration of all frequency deviations.  Each QSE should monitor its units to verify that these elements do not contribute to a governor droop characteristic greater than five percent (5%).