## ERCOT Operations Report

## ROS & OWG

## March 2005

Frequency control   59.9 > F > 60.1

| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| --- | --- | --- | --- | --- | --- |
| 3/1/2005 6:11 | 59.895 | 31684 | 995 | -773 | QSE with large negative SCE due to scheduling error. |
| 3/2/2005 19:06 | 60.120 | 34835 | -935 | 74 | VDI issued to reduce generation/ Fast Time Error Correction |
| 3/4/2005 15:54 | 59.894 | 29438 | -72 | -426 | Trip previous to frequency dip |
| 3/6/2005 1:06 | 60.102 | 23306 | -130 | 196 | -540 (-260) |
| 3/6/2005 3:11 | 60.101 | 22354 | -146 | 375 |  |
| 3/6/2005 10:35 | 60.121 | 26866 | -575 | -236 | VDI issued to reduce generation |
| 3/6/2005 14:10 | 59.836 | 26773 | -34 | -673 | QSE with lost resource not sending updated generation information from 12:30 - 14:30. QSE Laar response signal incorrect for this event. |
| 3/6/2005 15:04 | 60.113 | 26322 | -579 | -113 | VDI issued to reduce generation. Sustained high frequency |
| 3/7/2005 3:10 | 59.894 | 21787 | 230 | -590 | Responsive Laar from released @ 03:09 |
| 3/7/2005 3:30 | 60.102 | 21835 | 197 | -33 | Instantaneous 125 MW load reduction across 03:30 |
| 3/9/2005 18:35 | 59.899 | 29897 | -16 | -695 |  |
| 3/17/2005 16:05 | 60.111 | 28365 | -580 | 412 | VDI issued to reduce generation |
| 3/20/2005 9:07 | 60.101 | 25502 | -577 | 170 | 525 (250) |
| 3/27/2005 9:04 | 60.119 | 28966 | -580 | 185 | 930 (425) VDI issued to reduce generation |

| Disturbance Data |  |  |
| --- | --- | --- |
| 3/3/2005 18:56 | 59.854 | 480 MW/ 3 CC units at station |
| 3/4/2005 15:47 | 59.774 | 770 MW |
| 3/6/2005 14:02 | 59.774 | 770 MW |
| 3/7/2005 3:02 | 59.8 | 525 MW |
| 3/7/2005 3:14 | 59.889 | 275 MW |
| 3/7/2005 18:47 | 59.898 | 160 MW |
| 3/14/2005 2:38 | 59.81 | 470 MW |
| 3/20/2005 4:13 | 59.88 | Approximately 255 MW of generation lost on private network |
| 3/26/2005 16:59 | 59.85 | 942 MW/ 7 units at station |
| 3/29/2005 17:21 | 59.888 | 555 MW runback & trip |

Deployed Responsive (30) (Reported Above)

| 3/1/05 6:07 | 3/7/05 3:02 | 3/14/05 2:38 | 3/24/05 12:51 | 3/27/05 18:55 |
| --- | --- | --- | --- | --- |
| 3/3/05 16:51 | 3/7/05 3:10 | 3/17/05 8:02 | 3/24/05 22:01 | 3/27/05 19:01 |
| 3/3/05 18:48 | 3/7/05 18:47 | 3/20/05 4:13 | 3/25/05 5:00 | 3/27/05 20:02 |
| 3/4/05 15:47 | 3/8/05 6:03 | 3/20/05 18:49 | 3/25/05 7:04 | 3/29/05 0:00 |
| 3/4/05 20:12 | 3/9/05 18:35 | 3/21/05 21:59 | 3/26/05 16:58 | 3/29/05 17:21 |
| 3/6/05 14:02 | 3/12/05 9:13 | 3/22/05 11:39 | 3/26/05 17:14 | 3/31/05 6:05 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Feb 05 | March 04 | March 05 |
| --- | --- | --- | --- |
| DFW | 8 | 38 | 0 |
| E RIO | 54 | 46 | 33 |
| W RIO | 29 | 33 | 30 |
| Laredo | 36 | 25 | 34 |
| Bryan Area | 13 | 0 | 1 |
| Corpus | 28 | 25 | 31 |
| Abilene | 0 | 62 | 0 |
| San Angelo | 0 | 19 | 0 |
| Western | 1 | 9 | 0 |
| Houston | 4 | 0 | 0 |
| Northeast | 7 | 0 | 0 |
|  | 180 | 257 | 129 |

OOME / Congestion Management Activity

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Garden Villa - Jefferson 138kV | South Channel - Jefferson 138kV | 7 |
| Heights - Freeway Park 138kV | Heights - PH Robinson 138kV | 5 |
| North Edinburg - Rio Hondo 345kV | Magic Valley Weslaco - Weslaco 138kV | 4 |
| Frontera - South McAllen 138 kV | North McAllen - West McAllen 138 kV | 3 |
| Gibbons Creek - Twin Oak 345kV | Jewett - Watson Chapel 138kV | 3 |
| Menard Auto 138/69kV | Ballinger-Paint Rock 69kV | 4 |
| North Edinburg - Rio Hondo 345kV | MVEC Weslaco - MVEC Heidelburg 138kV | 3 |
| Pharr - MVEC 138kV | North Edinburg-North Alamo 69kV | 3 |
| South - North OC1 |  | 3 |
| Tenaska - Concord 138kV | Tenaska - Concord 138kV | 3 |
| Martin Lake - Stryker Creek - Enterprise 345 | Elkton 345/138 kV Auto | 2 |
| Angleton - West Columbia 138kV | South Lane City - New Gulf 138kV | 1 |
| Bates - Frontera 138kV | Frontera - Sharyland 138kV | 1 |
| Burnett 138/69kV Auto | Buchanan 138/69kV Auto | 1 |
| Clear Spring-Marion-Zorn 345kV | Bandera LCRA - Verde Creek 138kV | 1 |
| Clear Spring-Marion-Zorn 345kV | Seguin- Sequin West 138kV | 1 |
| Clear Springs - Marion - Zorn 345kV | Loop 337 - Comal 138kV | 1 |
| Ennis West - Sterrett 138kV | Rockett - Rockett Switch 69kV | 1 |
| Gibbons Creek - Bryan - Greens Prairie 138 | Texas AM - Dansby 138 kV | 1 |
| Gibbons Creek - Twin Oak 345kV | Boonville - Sutton 69kV | 1 |
| Gibbons Creek T1 345/138kV | Jewett - Watson Chapel 138kV | 1 |
| Holt Sw -Permian Basin 138kV | North Odessa 138/69kV Auto | 1 |
| Ingleside-Dupont-Whitepoint 138kV | Aransas Pass-Port Aransas 69 kV | 1 |
| La Palma 345/138kV auto | Rio Hondo - La Palma 138kV | 1 |
| Military Hwy 138 / 69 kV Auto | Military Hwy 138/69kV Auto | 1 |
| North - Houston |  | 1 |
| North - West |  | 1 |
| Pharr Magic Valley – Val Verde 138kV | North Edinburg-Moore Field 69kV | 1 |
| Quanab AB Chem - Fairmont 138kV | Jefferson - South Channel 138kV | 1 |
| South - Houston |  | 1 |
| STP - Skyline & Hill Country 345kV | Blessing - Lolita 138kV | 1 |
| Vernon-Lake Pauline 138kV | Chillicothe-Vernon 69kV | 1 |

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

None

New Procedures/ Forms/Operations Bulletins

| Date | Operations Bulletin | Subject |
| --- | --- | --- |
| 3/29 | POB 163 | SS Desk - GMD Reporting |
| 3/17 | POB 162 | FC Desk - Maintenance Level 2 and 3 Outages |
| 3/17 | POB 161 | TS Desk - Maintenance Level 2 and 3 Outages |
| 3/16 | POB 160 | OP Desk - Execute the HA Study (timing). |
| 3/15 | POB 159 | OP Desk - Automated Offset Calculations. |
| 3/9 | POB 158 | TS Desk - VDI for Oklaunion. |
| 3/9 | POB 157 | FC Desk - Response to Frequency Decay. |
| 3/9 | POB 156 | TS Desk - Issue VDE (timing) |
| 3/7 | POB 155 | TS Desk - Western Area Voltage Support |
| 3/7 | POB 154 | FC Desk - Issue VDE (timing) |
| 3/7 | POB 153 | FC Desk - Use of LAARS to Arrest a Reportable Low Frequency Disturbance |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems

3/29 00:00 – 02:30    When total McCamey area generation approached 550 MW, area voltages sagged.  Voltage dips to .93 pu observed on the 138 kV system.  Voltages corrected as partial trips of wind farms reduced MVAR consumption.  The cycle continued as McCamey generation came back on line after the trips.

Blackout/Load Shed incidences

None

# Communication

3/15	Extended Ancillary Service Market to 14:00.

3/27    05:30 interval held.  MOS didn’t clear until 05:33.

Major Computer Problems, Enhancements & Fixes

None

ERCOT peak (Unofficial)

3/30	 17:00		36440

Update on New Generation

150 MW unit in Coast Zone.

OCN, Advisory, Alert, Emergency Notice and Major Events

| 3/5 | 00:05 - 04:30 | OCN | Insufficient BES bids 02:00-06:00 |
| --- | --- | --- | --- |
| 3/6 | 0:15 - 04:15 | OCN | Insufficient BES bids |
| 3/6 | 19:00-24:00 | OCN | Insufficient BES bids |
| 3/15 | 19:38 | Transmission Alert | Loss of Walnut Spring to Stephenville loads Lake Whitney - Olson |
| 3/16 | 23:45 | OCN | Capacity shortage 07:00 - 13:00 on 3/17 |
| 3/16 | 7:00 -23:25 | Transmission Alert | Loss of Walnut Spring to Stephenville loads Lake Whitney - Olson |
| 3/17 | 01:24 - 3:00 | Alert | Capacity shortage 08:00 - 12:00 |
| 3/17 | 0:00 - 1:25 | OCN | Capacity shortage 07:00 - 13:00 |
| 3/17 | 5:20 - 15:50 | Transmission Alert | Loss of Walnut Spring to Stephenville loads Lake Whitney - Olson |
| 3/21 | 12:09 | OCN | Insufficient BES bids 12:00-14:00 |
| 3/21 | 14:22-23:06 | Transmission Alert | Loss of Menard Tr loads Ballinger – Paint Rock |
| 3/21 | 16:43-23:06 | Transmission Alert | Loss of Bates Tr. Loads N Edinburg - Moore Field |
| 3/21 | 16:45-23:05 | Transmission Alert | Loss of Pharr - Val Verde Rd loads N Edinburg - N Alamo |
| 3/22 | 09:02-21:30 | Transmission Alert | Loss of Pharr - Val Verde Rd loads N Edinburg - N Alamo |
| 3/23 | 13:10 - 23:30 | Transmission Alert | Loss of Menard Tr loads Ballinger - Paint Rock |
| 3/26 | 02:00 - 03:00 | Transmission Alert | Loss of Hamilton - Balcones loads McNeil – Koenig |
| 3/30 | 15:00 - 22:45 | Transmission Alert | Loss of Frontera - S McAllen loads N McAllen - W McAllen |

3/21   06:25	345 kV bus cleared removing 4 lines and the transformer.  An additional 345 kV line and transformer tripped at a neighboring station.  All elements were returned to service by 07:02 with the exception of the first transformer, which returned at 07:08.

3/21   11:00	1 138 kV line, 1 345 kV line, and 1 unit near Abilene tripped.  The 345 kV line and unit returned to service within a few minutes.  The 138 kV line was reclosed within the hour.