Date: _________________

To: ___________________

Subject: Verification result of Reactive Capability  Limit Test

Having thoroughly examined your submittal of the Unit Reactive Capability Limit Verification Test, conducted on ________________,   ERCOT can not accept the test result because it failed to meet the current Protocols/Guide requirements listed below:

□	Lag test was not performed during peak load conditions [(ERCOT Protocols Requirement

6.10.3.5 (3)].

□	Lead test was not performed during low load conditions [(ERCOT Protocols/Guide Requirements

6.10.3.5 (4) and 3.1.4.3.2)]

□        Test result did not hold for 15 minutes [(ERCOT Protocols Requirement 6.10.3.5 (3)].

□        ERCOT has telemetered information for the test period described which suggests that the

test result is inaccurate or the telemetry to ERCOT is inaccurate and must be repaired. A

copy of our data is attached [(ERCOT Protocols Requirement 6.10.3.5 (2)].

□      Lag test was not performed at MW output > 95% of unit capability (_____MW test < .95*____capability)

[(ERCOT Protocols Requirement 6.10.3.5 (3)].

□        Lag test was not within 90% of CURL capability. Your CURL showed a capability

of   _________Mvar ; 90% of _____ Mvar is _____ Mvar and you only achieved_______

Mvar. (ERCOT Guide Requirement 3.1.4.3.4).

□	Lead test was not within 90% of CURL capability.  Your CURL showed a capability

of _____ Mvar; 90% of _____ Mvar is _____ Mvar and you only achieved ______.Mvar

[(ERCOT Guide Requirement 3.1.4.3.2)].

□	No CURL was provided or available at ERCOT to evaluate the test (ERCOT Guide

Requirement 3.1.4.3.2)

□      The information provided on the Biennial Unit Reactive Limits Verification Form is

incomplete (ERCOT Guide Requirement 3.1.4.3.3)

ERCOT recommends the following action(s) to resolve this issue.

□	Provide the required information.

□	Retest the unit as required by ERCOT Guides and Protocols.

□	Either retest the unit, or provide a CURL which reflects the limitation observed across the units

operating range.

Please identify clearly the “Estimated Reactive Capability Curve - CURL” you provide as described in ERCOT Guide 3.1.4.3.1.

If you have any questions, please contact you Account Manager, __________________, at 512-248-_____

cc. ERCOT Compliance