| PRR Number | 583 | PRR Title | Responsive Reserve Deployment |
| --- | --- | --- | --- |
| Date |  | 4/17/05 |  |
| Submitter’s Information |  |  |  |
| Name |  | Scott Wardle |  |
| E-mail Address |  | Scott_Wardle@oxy.com |  |
| Company |  | Occidental Energy Ventures, Corp. |  |
| Company Address |  | PO Box 27757, Houston, Tx 77227 |  |
| Phone Number |  | 713.215.7142 |  |
| Fax Number |  | 713.985.1453 |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT |  |  |  |
| MARKET SEGMENT |  |  |  |
| Consumer |  |  |  |
| LSE: General, Including NOIE |  |  |  |
| LSE: CR & REP |  |  |  |
| QSE |  |  |  |
| Resource |  |  |  |
| TDSP |  |  |  |

Comments

Occidental agrees in the spirit of this change, but disagrees with the rigidity of the language that leaves the operator with no optionality with how much RRS is deployed.  In a low frequency event where generation side RRS (33%) and Regulation Service has been depleted, immediately deploying all remaining Hydro and LAAR Resources may very well be the best solution.  However, whether this is the correct decision is dependent upon the rate of decline of frequency.  Immediately deploying all Hydro and LAAR Resources will have a dramatically different outcome in an instance where frequency is declining slowly versus one where it is rapidly decreasing.  Overdeployment could cause overshoot of the 60Hz target.  We feel the decision on how much LAAR and Hydro to deploy should be at the discretion of the operator, and have added simple language to include this option.

In addition, deploying all remaining LAAR could cause a situation where critical Resources are taken out of service, and may not be able to provide services for up to the limit of 3 hours.  It seems a more logical solution to deploy LAAR in stages.  This approach would help to minimize overshoot and keep as much reserve as possible.

Operations Bulletin 157 sets the criteria for LAAR deployment in a frequency decay situation at 59.85Hz and declining.  In this bulletin, it also requires the operator to deploy “ALL” LAAR.  Again, we feel the amount of deployment should be left to the discretion of the operator.

Lastly, comments on deploying 33% of RRS should be clarified so that it is clear we are talking about 33% the total 2300MW or the amount of generation side RRS procured by ERCOT.  Operations Bulletin 157 and Protocol 6.7.3 currently do not agree.

Note: Deploying Resources in stages would require a system to be set up to prevent Resources from discriminatingly being called upon.  We feel setting up a system would not be difficult, nor would its implementation.  The details could be worked out between ERCOT and the Market Participants.

Revised Proposed Protocol Language

6.7.3	Deployment of Responsive Reserve Service

(1)	Responsive Reserve energy shall be deployed as necessary to meet NERC requirements.  This shall be accomplished by:

(a)	Automatic generation action as a result of a significant frequency deviation;

(b)	Through use of an automatic signal and a Dispatch Instruction to deploy Responsive Reserve energy from Generation Resources; and/or

(c)	By Dispatch Instructions for deployment of Responsive Reserve energy from Load acting as a Resource via an electronic Messaging System to providers.

(2)	Deployment of energy as a result of automatic governor action will not be considered as an Uninstructed Deviation.

[PRR307: Revise Section 6.7.3(1) & (2) as follows when system change implemented.] 6.7.3 Deployment of Responsive Reserve Service (1) Responsive Reserve energy shall be deployed as necessary to meet NERC requirements. This shall be accomplished by: (a) Automatic Resource control/governor system action as a result of a significant frequency deviation; (b) Through use of an automatic signal and a Dispatch Instruction to deploy Responsive Reserve energy from Resources; and/or (c) By Dispatch Instructions for deployment of Responsive Reserve energy from Interruptible Load acting as a Resource via an electronic Messaging System to providers. (2) Deployment of energy as a result of automatic Resource control/governor system action will not be considered as an Uninstructed Deviation.

(3)	ERCOT will deploy Responsive Reserve Service in response to disturbance control assistance requirements as specified in the Operating Guides or after all the bids in the Balancing Energy Services Up Bid Stack have been depleted.  Energy from Responsive Reserve Resources will be deployed by ERCOT in accordance with Section 5.6, Emergency and Short Supply Operations.

(4)	ERCOT deployment of Responsive Reserve Service Resources will be proportioned first between suppliers who provide RRS using Generation Resources until thirty-three percent (33%) of the total amount procured from all Resources by ERCOT is deployed.  If deployment of more than thirty-three percent (33%) is required,  ERCOT shall:

(a)	For frequency restoration caused by an event other than capacity insufficiency, issue an Emergency Notice for frequency restoration and deploy additional RRS being provided by hydro Resources and/or by LaaR.

(b)	For frequency restoration related to capacity insufficiency, declare the EECP in effect and follow emergency provisions in Section 5, Dispatch.

(5)	ERCOT will deploy Balancing Energy Service and Non-Spinning Service as soon as practicable to minimize the use of Responsive Reserve energy.

(6)	All providers of Responsive Reserve Resources will be required to provide feedback to ERCOT of their availability and level of deployment in Real Time.  Except in those instances where a significant frequency deviation has occurred and temporary deployment is necessary to meet NERC requirements, ERCOT shall deploy Responsive Reserve Services according to Section 5.6, Emergency and Short Supply Operations.

(7)	Once Responsive Reserve Service is deployed, the Obligation to deliver energy shall remain until specifically instructed by ERCOT to stop providing energy from RRS, but not longer than the period of the service is scheduled.

(8)	The QSEs providing Responsive Reserve Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

[PRR496: Add (9) to Section 6.7.3 as follows when system change implemented.] (9) Responsive Reserve Service procured from a Load Acting as a Resource Block Bid shall be deployed as a block.