## Slide 1: August 18, 2004 DCS Event
Follow-up to Final Report

## Slide 2: Key Areas for Follow-Up Tracking and Reporting
What has been done to date with ERCOT’s action items?
  PDCWG reviewed August 18, 2004 DCS event report and provided comments on possible actions
  ERCOT has addressed procedures to manually deploy additional resources in a slow frequency recovery
  A PRR is in draft form to address EECP requirements
    PRR to be released soon for ERCOT internal review
    Addresses operator deployment of RRS once the first 33% has been automatically deployed
  Review ERCOT frequency bias and automatic RRS deployment strategy in progress
    No change recommended related to automatic RRS deployment
    PDCWG has suggested a lower bias

## Slide 3: Key Areas for Follow-Up Tracking and Reporting
What has been done to date on QSE action items?
  ERCOT Compliance will send out letters (February 4, 2005) to the QSEs based on the PDCWG’s suggestions
  Follow-up questions will explore whether the QSEs corrected the problems that caused a slow recovery
  Response letters due by February 18, 2005

## Slide 4: Key Areas for Follow-Up Tracking and Reporting
Other follow-up items
  Transmission Operator / TDSP
    TXU has addressed improved breaker testing isolation
    Developing process to identify field wiring changes
  Revise Protocol 6.10.5.4
    Current protocol measurements do not address QSE performance in DCS events
    Compliance will work with ROS to review

## Slide 5: Disturbance Control Performance Adjustment
NERC Resources Subcommittee (RS) met in late January
No waiver was given, but…
No additional RRS is required since ERCOT already carries more than necessary, 2300 MW
1250 MW RRS required, 109 MW penalty, equates to 1359 MW now required
2300 MW exceeds ERCOT’s requirement of 1359 MW

## Slide 6: EMMS and State Estimator Issues
Loss of telemetry/telemetry inaccuracy
  Generating plant tripped off line but telemetry did not change
  State estimator not likely to alert an operator on August 18th
Utilizing transmission data to supplement QSE data
  EMMS group developing ICCP feature as a backup to RTU data; not in service on August 18th
Did State Estimator (SE) show any problems?
  SE in service at time of event and working properly
  SE feeds Real-time Contingency Analysis (RTCA), which primarily addresses congestion

## Slide 7: Database Load on August 18
Database load occurred at 9:22:07
  Data quality suspect from 9:22:07 to 9:31:52
Database load occurred at 10:49:39
  Data quality suspect from 10:49:39 to 11:08:50
Second database load took place because of an issue with the database archive file
  Problem with network modeling
Issue has no known impact on frequency control (deployment of RRS, regulation)
Data quality was normal at the time of the event

## Slide 8: Questions?