## Slide 1: Reliability and Operations Subcommittee Report on Reliable Fuel Operations in ERCOT
Presentation to the
ERCOT Technical Advisory Committee
February 3, 2005

## Slide 2: Reliable Fuel Operations in ERCOT
ROS has developed the following assumptions:
Winter Peak Load – 45, 433 MW
  January 24, 2003
  Low temps. - coast 30 degrees, north 16 degrees.
Severe Winter Peak Forecast – 47, 704 MW
  5% severe weather adder

## Slide 3: Reliable Fuel Operations in ERCOT
According to the National Weather Service
1983 and 1989 are the coldest Decembers on record for the Houston area since 1889. The next coldest occurred in 1963.
Historical Forced Outage Rate for winter season – 10.5 to 11%

## Slide 4: Reliable Fuel Operations in ERCOT
Alternative Fuel Survey Results
  Natural Gas
    Primary Fuel of 82% of Registered Units in ERCOT
    Represents 75% of MW Capacity
  Solid Fuel (Lignite, Coal, Nuclear)
    Primary Fuel of 12%
    Represents 23% of MW Capacity
  Fuel Oil – 21, 798 MW
    Dual Fuel Capable 28%
    Represents 31% of MW Capacity

## Slide 5: Reliable Fuel Operations in ERCOT
Fuel Oil Continued:
Operational Dual Fuel Units – 81%
  Oil Start-up 48%
  Represents 31% of MW Capacity
  Gas Co-fired 39%
  Represents 59% of MW Capacity
Fuel Oil Testing
  Regularly Test 51%
  Represents 53% of MW Capacity

## Slide 6: Reliable Fuel Operations in ERCOT

## Slide 7: Reliable Fuel Operations in ERCOT

## Slide 8: Reliable Fuel Operations in ERCOT
Variables:
Generation – no obligation to serve
Maintenance Schedules – no coordination of planned Resource maintenance
Loads – Relaxed Balanced Schedules
ERCOT Emergency Procedures – no notification in advance of need for oil
Gas curtailments of generation can also curtail some loads.

## Slide 9: Reliable Fuel Operations in ERCOT
Variables continued:
While there are known gas capability or supply problems during periods of high demand, there are market incentives to continue to build efficient gas units.
The market incentive to “mothball” older units with poor heat rates may also reduce those units with dual fuel capability.

## Slide 10: Reliable Fuel Operations in ERCOT
Based on survey results, available oil capacity would be exceeded at a 47, 704 peak load (peak mw less amount of expected solid fuel plus hydro) if there were more than a 51% curtailment of the projected gas requirement.
Any loss of gas supply beyond this implies load shedding and likewise, any less oil capacity or solid fuel capacity also implies load shedding. This calculation is subject to any applicable FOR adjustment.

## Slide 11: Reliable Fuel Operations in ERCOT
Recommended Solutions:
Re-examine ERCOT Emergency Procedures
Gas transmission system status – improvements, pre-determined priorities for users, etc.
Review possibility of market incentives and regulatory relief to augment reliable fuel operations.