## Slide 1: Houston Area Constraint Mitigation Project
TAC – 3/3/2005

## Slide 2: Description of Project
Upgrade Jewett-Tomball/TH Wharton 345kV double circuit to 1450 MVA rating ($9.5M)
Construct new Hillje 345kV switching station in the STP-Holman 345kV line ($10.8M)
Build new Parish –Hillje 345kV double circuit (2-1590 ACSR) ($79.25M)
Add STP-Hillje 345kV circuit (2-795 ACSR) on open tower position of existing STP-Parish line ($8.35M)
Replace autotransformers at Greens Bayou #2 (800MVA), Tomball (600MVA), Addicks (800MVA and O’Brien #3 (600MVA) ($12.2M)
Upgrade O’Brien – O’Brien Tap 138kV circuits to 545 MVA ($0.2M)
Replace miscellaneous breakers and terminal equipment ($1.66M)

## Slide 3: Cost and Savings of Project
Jewett-Tomball/TH Wharton upgrade and autotransformer change outs scheduled in-service in 2007
Remainder of package scheduled in-service in 2008
Total cost of package of projects is $122 million
Projected production cost savings (in nominal $millions):
Annual savings of ~$60M significantly exceeds the $20M annual carrying cost of the project
2007 | 2008 | 2009 | 2010
14.5 * | 57.4 | 60.9 | 69.6

## Slide 4: Project Justification
Cumulative cost savings exceed the cumulative incurred cost of the line within 3 years
ERCOT also examined the sensitivity of these savings to the retirement of the TX Genco units and to lower gas prices. In all cases the project was still justified.

## Slide 5: Options Considered
Centerpoint evaluated 28 different packages of projects
ERCOT performed an economic evaluation of over 90 different combinations of these projects
Other projects that were evaluated include:
  Zenith – Salem 345kV Double Circuit
  Zenith – Salem – TNPOne 345kV Double Circuit
  O’Brien – Holman 345kV Double Circuit
  O’Brien – Fayette 345kV Double Circuit
  STP – O’Brien 345kV Single Circuit
  STP – O’Brien – Gibbons Creek 345kV Single Circuit
  STP – Parish additional circuit
  Loop STP - Holman 345kV circuit into Parish
  Upgrade Lolita – Blessing – Lane City
  Upgrade Bellaire – Smithers
  Upgrade Fayetteville auto and Fayetteville – Bellville South line

## Slide 6
The Stakeholder review period for this project was held in September 2004. Comments supporting the package of projects were received from:
      TXU Energy
      Austin Energy
      Direct Energy
      STEC – supported, however, did not believe STEC portion of package was required
A second comment period was held in January 2005 on the economic analysis performed by ERCOT. Comments supporting the results were received from:
      Centerpoint Energy
      Reliant Energy
      TXU Energy
      City Public Service of San Antonio
      Austin Energy
      Constellation
      AEP
Stakeholder comments at all stages of the review have been in support of the project, with no dissenting comments.
Stakeholder Review

## Slide 7
ERCOT supports the need for this project, as described, and asks that TAC endorse approval by the Board
ERCOT Support For the Project