## ERCOT Operations Report

## ROS & OWG

## April 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 4/11/2005 6:58 | 60.111 | 29693 | 134 | 152 | 1825 ( 640) |
| 4/11/2005 22:04 | 60.149 | 30889 | -968 | 322 | -3700( - 670), 400 MW VDI |
| 4/12/2005 1:09 | 60.118 | 22913 | -556 | 340 | 300 MW VDI |
| 4/17/2005 22:54 | 60.116 | 27660 | -970 | 500 | -800(-350), 500 MW VDI |
| 4/19/2005 2:40 | 60.105 | 22791 | 107 | 239 | Nonconforming load |
| 4/20/2005 0:06 | 60.102 | 26401 | 243 | 337 | -1460(-700), Nonconforming load |
| 4/23/2005 2:36 | 60.150 | 23331 | -554 | -68 | 30+ minutes high frequency/SCE, 500 MW VDI |
| 4/23/2005 22:35 | 60.107 | 26538 | -938 | 500 |  |
| 4/28/2005 15:31 | 59.899 | 40255 | 785 | -700 | Hour Ahead study ran multiple times due to incorrect results. Incorrect load forecast read in to study. |
| 4/30/2005 1:15 | 60.110 | 25542 | -556 | 73 | 150 MW VDI |
| 4/30/2005 21:59 | 60.101 | 27565 | -202 | 397 | -2500(-675) |

| Time | Frequency | MW Loss |
| --- | --- | --- |
| 4/8/2005 11:22 | 59.812 | 585 |
| 4/8/2005 18:45 | 59.847 | 575 |
| 4/9/2005 23:29 | 59.861 | 320 |
| 4/23/2005 15:01 | 59.882 | 400 |
| 4/28/2005 11:54 | 59.895 | 550 |
| 4/29/2005 23:11 | 59.880 | 510 (3 CC units) |

Deployed Responsive (28) (Reported Above)

| 4/4/05 20:57:06 | 4/11/05 20:08:54 | 4/18/05 18:39:38 | 4/23/05 23:20:46 |
| --- | --- | --- | --- |
| 4/7/05 8:20:40 | 4/11/05 23:56:50 | 4/21/05 15:01:08 | 4/26/05 6:01:20 |
| 4/7/05 8:24:56 | 4/12/05 0:28:54 | 4/21/05 15:14:34 | 4/28/05 11:54:06 |
| 4/8/05 11:21:30 | 4/12/05 0:32:46 | 4/23/05 0:04:32 | 4/28/05 15:19:58 |
| 4/8/05 18:45:50 | 4/13/05 0:04:42 | 4/23/05 3:19:14 | 4/28/05 15:43:58 |
| 4/9/05 23:29:42 | 4/17/05 0:46:16 | 4/23/05 11:01:32 | 4/28/05 15:53:40 |
| 4/10/05 21:56:56 | 4/17/05 22:00:16 | 4/23/05 15:01:26 | 4/29/05 23:11:24 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | April 04 | March 05 | April 05 |
| --- | --- | --- | --- |
| DFW | 77 | 0 | 33 |
| E RIO | 48 | 33 | 40 |
| W RIO | 6 | 30 | 29 |
| Laredo | 47 | 34 | 37 |
| Bryan Area | 0 | 1 | 2 |
| Corpus | 27 | 31 | 30 |
| Abilene | 41 | 0 | 0 |
| San Angelo | 30 | 0 | 0 |
| Western | 6 | 0 | 2 |
| Houston | 1 | 0 | 2 |
| San Antonio | 19 | 0 | 1 |
|  | 302 | 129 | 176 |

OOME / Congestion Management Activity

| Contingency | Overloaded Element | # Occurences |
| --- | --- | --- |
| Gibbons Creek - Bryan East & Bryan Greens Prairie | Dansby - TAM 138kV | 14 |
| Frontera - South McAllen 138kV | North McAllen - West McAllen 138kV | 10 |
| North Edinburg - Rio Hondo 345kV | MV Weslaco-MV Heidelburg | 7 |
| Sargent Rd. - Watermill Switch 345kV | Watermill 345/138kV Auto | 6 |
| Bates - Frontera 138kV | Frontera - Sharyland 138kV | 5 |
| Cico - Pipe Creek 138kV | Cico - Comfort 138kV | 4 |
| Coleto Creek - Kenedy Switch 138kV | Leon Creek - Pleasanton 138kV | 4 |
| Odessa EHV - Moss Switch 345kV | Odessa - Huntsman 138kV | 4 |
| Clear Spring - Marion - Zorn 345kV | Loop 337 - Comal 138kV | 3 |
| Falfurrias - North Edinburg 138kV | Alice - North Ella 69kV | 3 |
| Lytton Springs - Zorn & Austrop - Zorn 345kV | Zorn - Luling 138kV | 3 |
| North Edinburg - Rio Hondo 345kV | Alberta Road Tap - Pharr MVEC 138kV | 3 |
| North Edingburg - Rio Hondo 345kV | South McAllen - Las Milpas 138kV | 3 |
| West Ennis - Sterrett 138kV | Trumbull 138/69kV auto | 3 |
| Allen Sw-Royse Sw-Monticello 345kV | Rockwall -Rockwall Tap 138kV | 2 |
| Clear Spring-Marion-Zorn 345kV | Cico - Comfort 138kV | 2 |
| Ennis West - Sterret 138kV | Trumbull 138/69kV Auto | 2 |
| Forney-Elkton & TriCorner 345kV | Watermill - Cedar Hill 345kV | 2 |
| Graham-Sweetwater / Abilene Mulberry Creek | Graham - Murray TU 138kV | 2 |
| Marion - Zorn & Clear Springs 345kV | Seguin - Seguin West 138kV | 2 |
| Morgan Creek-Odessa 345kV | Ft Lancaster-Illinois #4 69kV | 2 |
| Odessa EHV - Moss Sw 138kV | Huntsman - Rexall 138kV | 2 |
| Pharr Magic Valley EC-Polk Ave 138kV | North McAllen-West McAllen 138kV | 2 |
| RockPort-Rincon T1 138/69kV | Rincon-Gregory 69kV | 2 |
| Sargent Road - Watermill SW 345kV | Watermill SW - Cedar Hill SW 345kV | 2 |
| Big Brown SES - Venus Switch 345kV | Cedar Hill - Watermill 345kV | 1 |
| Big Lake 138/69kV Auto | Fort Lancaster - Illinois #4 69kV | 1 |
| Big Lake - North McCamey Sw 138kV | Fort Lancaster - Illinois #4 69kV | 1 |
| Big Lake 138/69kV auto | Illinois #4 - Ozona 69kV | 1 |
| Big Lake-North McCamey Sw 138kV | Forth Lancaster-Illinois #4 69kV | 1 |
| Clear Spring-Marion-Zorn 345kV | Seguin - Seguin West 138kV | 1 |
| Elkton-TriCorner-Martin Lake 345kV | Tyler SE - Tyler GE 138kV | 1 |
| Ennis Switch - Desoto switch 138kV | Sterrett - MG Industries 138kV | 1 |
| Enterprise - Trindad & Martin Lake - Stryker Creek | Nacogdoches 345/138kV Auto | 1 |
| Greenbelt - Caddo 138kV | Greenbelt - Tejas 138kV | 1 |
| Heights Sub - Freeway Park 138kV | Heights Sub - PH Robinson 138kV | 1 |
| Monticello - Allen - Sulphur Springs 345kV | Farmersville - Monticello 345kV | 1 |
| Morgan Creek-Eskota 138kV | Eskota 138/69kV Auto | 1 |
| North Edinburg - Bates 138kV | North Edinburg - McColl Rd. 138kV | 1 |
| North Edinburg - Rio Hondo 345kV | Weslaco - Heidelberg 138kV | 1 |
| North Edinburg - Rio Hondo 345kV | Magic Valley - Weslaco 138kV | 1 |
| North Edinburg-Rio Hondo 345kV | Weslaco - Rio Hondo 138kV | 1 |
| North Edinburg-Rio-Hondo 345kV | Weslaco switch - Magic Valley Weslaco | 1 |
| Pawnee - Calaveras 345kV | Leon Creek -Pleasanton 138kV | 1 |
| Pharr MVEC - MVEC Val Verde 138kV | North Edinburg - North Alamo 69kV | 1 |
| Pharr-Magic Valley EC-Polk Ave 138kV | West McAllen - North McAllen 138kV | 1 |
| Sandow 345/138kV Auto | Sandow - Elgin Switch 138kV | 1 |
| Sandow - Temple Sw. 345kV | Rockdale - Sandow 138kV | 1 |
| Somerset - Lytle 138kV | Leon Creek - Pleasanton 138kV | 1 |
| Tricorner-Martin lake&Forney Sw-Elkton 345kV | Elkton 345/138kV Transformer | 1 |
| West Columbia Main - Sweeny Cogen 138kV | Sweeny Sub - Clemons Tap 69kV | 1 |

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

4/15 	Revised Marion SPS.

New Procedures/ Forms/Operations Bulletins

| 04/08/2005 | MOB 25 | OOM Tool |
| --- | --- | --- |
| 04/08/2005 | MOB 24 | Resource Spcific Bid Limits |
| 04/08/2005 | MOB 23 | Resource Plan Enhancements |
| 04/08/2005 | MOB 22 | RPRS Market Redesign |
| 04/22/2005 | POB 166 | FC Desk - Approve NERC Tags for DC Ties |
| 04/18/2005 | POB 165 | T&S Desk - Issue an Advisory. |
| 04/18/2005 | POB 164 | T&S Desk - Procedure for Control of Transmission System Loading Within N-1 Thermal Contingency Criteria Using Real Time Contingency Analysis. |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems, Blackout/Load Shed incidences

None

Communication, Major Computer Problems, Enhancements & Fixes

4/21 10:00 – 4/22 23:00	Beginning with the 10:30 interval, XML messages were sent out as null instead of a message body.  Deployments and other information were given verbally to 5-7 QSE every interval.

ERCOT peak (Unofficial)

4/28	18:00	41,475

OCN, Advisory, Alert, Emergency Notice and Major Events

| 02-Apr-05 | 00:15 - 02:15 | Alert | Max capability of the units in the resource plan lower than forecasted load 0900 - 1200. |
| --- | --- | --- | --- |
| 05-Apr-05 | 16:24 - 19:30 | Transmission Alert | Loss of Frontera - S McAllen loads North McAllen - West McAllen 138kv line. |
| 06-Apr-05 | 16:15 - 21:00 | Transmission Alert | Loss of Frontera - S McAllen loads North McAllen - West McAllen 138kv line. |
| 07-Apr-05 | 14:54 - 21:45 | Transmission Alert | Loss of Frontera - S McAllen loads North McAllen - West McAllen 138kv line. |
| 07-Apr-05 | 14:41 - 22:00 | Transmission Alert | Loss of Menard Tr loads Ft Mason - Mason 69 kV. |
| 08-Apr-05 | 14:05 | Alert | Insufficient A/S bids for down regulation at 0600 |
| 08-Apr-05 | 19:05 | Transmission Alert | Loss of Bates 138/69 Tr islands 69 kV system about Bates. |
| 12-Apr-05 | 08:30 |  |  |
| 11-Apr-05 | 19:09-21:02 | Transmission Alert | Single contingency loads Ballinger to Paint Rock 69 kV. |
| 20-Apr-05 | 9:15 |  | Venus SPS activated |
| 20-Apr-05 | 15:27-18:09 | Transmission Alert | Loss of Kenedy - Coleto Creek loads Cuero-Cuero 69kv line. |
| 21-Apr-05 | 15:00 - 16:00 | Transmission Alert | Loss of Allen - Royse & Monticello 345kv loads Rockwall - Rowlett Tap 138kv |
| 21-Apr-05 | 15:00-18:07 | Transmission Alert | Loss of Coleto Creek - Kenedy 138kv loads Leon Creek-Pleasanton 138 line. |
| 22-Apr-05 | 15:30 -21:00 | Transmission Alert | Loss of Gibbons Creek - East/Greens Prairie loads Texas A&M-Dansby 138 KV. |
| 25-Apr-05 | 15:00-20:00 | OCN | Possibility of severe weather in North Texas and the Houston areas. |
| 28-Apr-05 | 5:30 | OCN | Capacity insufficiency for HE 17:00 - 21:00 |