| OGRR Number | 164OGRR | OGRR Title | Responsive Reserve MW Limit |
| --- | --- | --- | --- |
| ###### Date |  | April 11, 2005 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | PDCWG – Sydney L. Niemeyer Chair |  |
| E-mail Address |  | Sydney_l_Niemeyer@txgenco.com |  |
| Company |  | Texas Genco, LLP |  |
| Company Address |  | 12301 Kurland Drive, Houston, TX 77034 |  |
| Phone Number |  | 713-795-6108 |  |
| Fax Number |  | 713-795-7488 |  |

Comments

The PDCWG does not support this change due to the greater risk of firm Load Shedding as stated in ERCOT’s comments to the original OGRR161 dated 1/14/05.

The PDCWG agrees with ERCOT’s following statement:

“The purpose of Responsive Reserve Service (RRS) is to stabilize system frequency and to return the frequency to normal in a timely manner after a disturbance event.  Currently, the RRS is limited to 20% of Net Generation capability of an individual Generation Resource.  This OGRR would change this limit to 20% or 50 MW, whichever is greater.”

“ERCOT does not support this change for two reasons:”

“Greater risk of firm Load shedding-   The 20% of a unit’s Net Generation Capability Responsive Reserve limit is based on the requirement of a generator to have its governor in service and set within a 5% droop characteristic.    A generator droop response of 5% means that for a 3 Hz change in frequency a generator can move from no Load to full Load.  The first firm Load shedding relay point is set at a frequency of 59.3 Hz.  This means that for a 0.6 Hz change in frequency (right above firm Load shedding) only the first 20% of a unit’s capacity would be effective in stabilizing frequency above firm Load shedding.  Increasing the amount of a unit’s capacity that can be counted as Responsive Reserve above 20% would result in fewer units capable of stabilizing frequency above the firm Load shedding frequency point, and place ERCOT at greater risk of shedding firm Load.”

The PDCWG would like to add the following comparison of ERCOT frequency response if OGRR 164 were to be adopted: (see Table on next page)

|  |  |  | OGRR 164 |  |  | Now | OGR 164 |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Responsive Reserve |  | Responsive Reserve |  |  | 5% Droop | 5% Droop |
|  | Using 20% of HSL Limit |  | Using 20% or 50 MW |  |  |  |  |
|  | 20% RR (MW) | HSL Net MW | 50MW RR | HSL |  | MW/0.1 Hz | MW/0.1 Hz |
| Unit 1 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 2 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 3 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 4 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 5 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 6 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 7 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 8 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 9 | 12 | 60 | 50 | 60 |  | 2.00 | 2.00 |
| Unit 10 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 11 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 12 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 13 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 14 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 15 | 30 | 150 | 50 | 60 |  | 5.00 | 2.00 |
| Unit 16 | 61 | 305 | 50 | 60 |  | 10.17 | 2.00 |
| Unit 17 | 61 | 305 | 50 | 60 |  | 10.17 | 2.00 |
| Unit 18 | 60 | 300 | 50 | 60 |  | 10.00 | 2.00 |
| Unit 19 | 120 | 600 | 50 | 60 |  | 20.00 | 2.00 |
| Unit 20 | 120 | 600 | 50 | 60 |  | 20.00 | 2.00 |
| Unit 21 | 120 | 600 | 50 | 60 |  | 20.00 | 2.00 |
| Unit 22 | 160 | 800 | 50 | 60 |  | 26.67 | 2.00 |
| Unit 23 | 160 | 800 | 50 | 60 |  | 26.67 | 2.00 |
| Total | 1150 | 5750 | 1150 | 1380 |  | 191.67 | 46.00 |

In the above table, the required Responsive Reserve Service, per OGRR 164, could be supplied by 23 units with a HSL of 60 MW and a LSL of 10 MW.  This would provide 1150 MW of RR Service, but the best possible Frequency Response (at 5% droop) of these units would be 46 MW/0.1 Hz as compared to the present requirement of 191.67 MW/0.1 Hz.  This is approximately a 76% reduction in ERCOT’s frequency response.  Presently to provide 1150 MW of RR Service requires that a minimum of 1150/0.2 = 5750 MW of On Line capacity.  At 5% droop, 5750/30 = 191.67 MW/0.1 Hz. This is the minimum frequency response that should be provided under present policy by Responsive Reserve Service providers.

This example clearly demonstrates that OGRR 164 is an un-acceptable risk for Firm Load Shed.

Revised Proposed Operating Guide Language