| OGRR Number | 166 | OGRR Title | Double Circuit Contingencies |
| --- | --- | --- | --- |
| ###### Date |  | May 17, 2005 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | John Adams |  |
| E-mail Address |  | jadams@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | 2705 West Lake Drive |  |
| Phone Number |  | 512 248-3130 |  |
| Fax Number |  | 512 248-3055 |  |

Comments

The “Reason for Revision” description is misleading.  It states that “ERCOT currently deploys energy as if all double circuits would cause cascading outages 24 hours a day, 7 days a week”.  This is incorrect.  A correct statement would be: “ERCOT currently deploys energy as if any 345 kV double circuit outage over ½ mile in length which creates overloads above equipment Emergency rating(s) and does not have an identified Remedial Action Plan is a High Outage Consequence as defined by ERCOT Operating Guide 4.3.”  ERCOT believes this action is required because its studies indicate that the double circuit contingency will result in equipment damage or failure if there is no specific, predefined operating procedures in place which can mitigate the post-contingency violation within the time of the emergency rating.  ERCOT also deploys energy for select lower voltage double circuit outages over ½ mile in length meeting the criteria described above.

ERCOT notes two revisions contained in the OGGR not noted as changes and has highlighted these in the language below.  In the 2nd paragraph of changes, the word “only” was apparently added without being identified as an edit in the sentence: “The Forced Outage of a double-circuit transmission line (DCKT) will only be considered a credible single contingency for energy deployment decisions such as OOME and Zonal Balancing Energy for any of the following operating conditions…”  Under Bullet 3 under “High Outage Consequence,” it appears that four words were inadvertently deleted at the end of the sentence without those deletions being identified as an edit.  “Studies affirmatively indicate Outage of the DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures in time to prevent equipment damage or failure.”

Cascading Outages:

The statement in Bullet 2 of “High Outage Consequence” that ERCOT must have studies that affirmatively indicate that the outage of the DCKT would result in cascading outages or voltage collapse is problematic.  In practice, ERCOT’s existing software cannot prove by analysis that a contingency will result in cascading outages.  To do so requires multiple successive studies to determine which elements overload or reach unacceptable voltages after an overloaded element relays out of service or fails.

Given that ERCOT does not have the ability to affirmatively predict cascading outages in Real Time operations, this proposed provision contradicts NERC standard TOP-004 which states “If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliability power system limits within 30 minutes.”

Section 5.2.2 of the ERCOT Protocols requires ERCOT to operate in compliance with NERC Standards, Policies, Guidelines, and Operating Procedures.

Impact upon ERCOT Operating Procedure:

The 3rd bullet under “High Outage Consequence” states that ERCOT will consider “a double-circuit transmission line as a credible single contingency for energy deployment decisions such as OOME and Zonal Balancing Energy for any of the following operating conditions characterized by high DCKT Outage probability or consequence [if]:

- Studies affirmatively indicate Outage of the DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures in time to prevent equipment damage or failure."

ERCOT already performs in accordance with this requirement.  Therefore, ERCOT feels this OGRR, as written, requires no change in ERCOT’s current operating procedures.

Proposed Operating Guide Language Revision

## 4.3	Operation To Maintain Transmission System Security

ERCOT Operators are responsible for operating the ERCOT Transmission systems within first contingency transfer limits so that there is no overload of any significant transmission element whose loss could jeopardize the reliability of the ERCOT System. Whenever the ERCOT System is not engaged in emergency operation, it will be operated in such a manner that the occurrence of a single contingency will not cause any of the following:

a.	Uncontrolled breakup of the transmission system,

b.	Loading of Transmission Facilities above defined emergency ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures,

c.	Transmission voltage levels outside system design limits which can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs, or

d.	Customer outages, except for high set interruptible and radially served loads.

“Single contingency” criteria are specified as follows:

A credible single contingency is defined as the Forced Outage of two generating units in the ERCOT System within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer).

The Forced Outage of a double-circuit transmission line (DCKT) in excess of 0.5 miles in length will always be considered a credible single contingency for all security constrained unit commitment decisions such as OOMC and Replacement Reserve Service.

The Forced Outage of a double-circuit transmission line (DCKT) will only be considered a credible single contingency for energy deployment decisions such as OOME and Zonal Balancing Energy for any of the following operating conditions characterized by high DCKT Outage probability or consequence:

High Outage Probability

- Severe weather conditions are forecasted by ERCOT in the vicinity of the DCKT.

- Weather conditions indicate a high risk of insulator flashover on the DCKT.

- Individual circuits that are part of the DCKT have experienced repeated Forced Outages within the preceding 48 hours possibly indicating unresolved problems.

- A high risk of DCKT Outage exists due to fire in progress near the DCKT right-of-way.

High Outage Consequence

- Another transmission Facility, which significantly increases the impact of an Outage to the DCKT, is out of service.

- Studies indicate Outage of the DCKT would result in cascading outages or voltage collapse.

- Studies affirmatively indicate Outage of the DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures in time to prevent equipment damage or failure.

The Control Area Authority can order the following actions when the above criteria is not met if such actions assist the TDSP in meeting their responsibilities:

| EMERGENCY CONDITION | CONTROL AREA AUTHORITY ACTION |
| --- | --- |
| Significant Transmission Overload | - The Control Area Authority can order adjustment to unit generation schedules (unit specific balancing instructions), switching of transmission elements or load interruption to relieve a severely overloaded transmission element. - The Control Area Authority can order a transmission element whose loss would not have a significant impact on the reliability of ERCOT transmission system switched out to increase interconnected system transfers. |
| Violation of “First Contingency” Criteria | The Control Area Authority can order changes to unit dispatch or commitment to eliminate a “first contingency” criteria violation. Normally these changes should be performed via the market control mechanisms of constraint management as described in the ERCOT protocols, but ERCOT operators have the authority to issue valid Dispatch Instructions independent of these systems. |
| Violation of Voltage/Reactive Criteria | The Control Area Authority can order changes in unit dispatch if coordinated voltage and Reactive Power criteria that are considered critical to interconnection reliability are violated for the existing or first contingency conditions. |
| Total or Partial System Blackout | Implement Black Start Procedure |

TDSP operators are responsible for operating the sub-transmission system within safe operating limits, for maintaining the transmission system, for performing all switching operations after coordinating with ERCOT, and for notifying ERCOT operators of threats to, or overloads of the transmission system under their supervision.