## Slide 1
Congestion Management
Beth Garza
bgarza@ercot.com
512-248-6361

## Slide 2: Session Objectives
What are the tools used by ERCOT to manage congestion?
How do QSE and TO operator actions affect ERCOT’s ability to manage congestion?
What is a Remedial Action Plan?
What is a Mitigation Plan?

## Slide 3: ERCOT Objectives
Congestion must be managed, and it costs $$$!
Keep flows under limits,
    Or ELSE
  Equipment may be damaged
  System is insecure
Allow economical dispatch
  Allow power to flow without intervention, subject to reliability.

## Slide 4: Two Types of Congestion
Congestion on CSCs or CREs that can be resolved by zonal deployment of Balancing Energy Services (BES)
Controlled on a QSE portfolio basis
ERCOT software determines the optimal inter-zonal portfolio balancing instructions to relieve CSC congestion
BES instructions used to solve zonal congestion and/or energy imbalance are Category 1 instructions
Cost of solution is assigned directly to the QSEs whose schedules impact the CSCs
Zonal

## Slide 5: 2005 Zones and CSCs
6
5
2
4
3
1
W
N
NE
S
H
2: Sandow – Temple (2)
3: STP – Dow (2)
4: Jewett – THWarton Gibbons Creek - O’Brien
5: Farmersville – Royse (2)
1: Graham – Parker/Benbrook
6: Parker/Benbrook - Graham

## Slide 6: Two Types of Congestion
Local
Not defined by a CSC or CRE
Controlled with resource-specific deployment or OOM instructions
ERCOT software (SPD) determines resource-specific instructions that best accomplish congestion relief. Resource-specific instructions may be:
  Category 2: At or below a MW level
  Category 3: At or above MW level
  Category 4: Go to a specific MW level

## Slide 7: Congestion Shadow Price
20MW
10MW
30MW
5MW
15MW
10MW
Lower
Raise
Incremental system cost ($) to decrease flow in direction of constraint by 1 MW
A non-zero shadow price on a CSC means that some balancing energy (zonal re-dispatch) was required to relieve congestion
Calculated by ERCOT system component called “SPD”
Limiting Element

## Slide 8: Scheduling, Pricing & Dispatch
Scheduling, Pricing and Dispatch = SPD
Executes every 15 minutes to deploy Balancing Energy
Calculated CSC flows
Calculated flow for OC2 constraints
Portfolio Balancing Awards and resource specific instructions
Zonal MCPEs
Inputs
Outputs
Telemetered Generator MW output
Shift factors
Forecasted load
QSE Energy Schedules
QSE Resource Plan data
OC1 and OC2 constraint limits
SPD
ERCOT Market Operating System
* Note: Real time (Physical) limits are not visible to SPD
Notes: SPD Solves an optimization function:
Min (Total cost for deploying BES)
Subject to:
Power Balance Constraint
Zonal Congestion Constraint
Ramp Rate Constr
Resource Plan Constr
BES Bid Constr

## Slide 9: Types of Constraints Used by SPD
Real-time
Automatically created limit used in local congestion.
Local
OC3
Real-time
Limit may be changed in adjustment or operating period based on impending congestion conditions
Local
OC2
Real-time
SPD limit may be changed in adjustment or operating period based on impending congestion conditions
Setting of 9999 indicates constraint not active
Zonal
CSC / CRE
OC1
Monthly
Based on planning studies taking into account planned outages, flow patterns
Basis of TCRs and CSC congestion notices
Suppressed in favor of OC1 in Real-time Balancing
Zonal
CSC
OC0
Frequency
Description
Applicability
Limit

## Slide 10
Transmission Limits to Be Monitored
For: Tuesday 03/29/2005
The maximum total loading on the following Zonal and Local Constraint monitored elements should be maintained. Local constraints will be resolved with Real Time Contingency Analysis
Time | South to North SDSES–TMPSW (S1) __ Potential IROL | Northeast to North (Sum of 2 Farmerville - Royse) (S2) Potential IROL | South to Houston (Sum of 3 STP-DOW & STP-WAP) (S3) __ Potential IROL | West to North Graham – Parker/ Benbrook (S4) Potential IROL | North to West Benbrook/Parker – Graham (S5) Potential IROL | North to Houston Gibbons Creek – O’brien Jewett – T.H. Wharton Jewett – Tomball RNS – Kuykendahl (S6) _Potential IROL
00:00- 09:00 | 890 | 1700 | 1520 | 810 | 850 | 3030
09:00- 12:00 | 890 | 1700 | 1520 | 810 | 850 | 3030
12:00- 16:00 | 890 | 1700 | 1520 | 810 | 850 | 3030
16:00- 24:00 | 890 | 1700 | 1520 | 810 | 850 | 3030
South => North | Loss of Double Sandow SES–Temple SW 345kV loads Roundrock – Chief Brady
Northeast => North | Loss of Carrollton NW – Collin 345 loads Collin SES – Frisco 138kV line.
South => Houston | Dbl STP-Dow STPDOW18 & STPDOW27 345kV loads Waller – Prairie View 138kV.
West => North | Loss of Graham – Benbrook & -Parker 345kV loads Parker SW – Willow Creek 345kV line.
North => West | Loss of Graham –Benbrook & --Parker Sw 345kV loads Stephenville –Lingleville 138kV.
North=>Houston | Loss of Dbl Jewett - TH Wharton & --Tomball 345kV loads Waller – Prairie View 138kV.
Calculated by: Jose Gaytan
Above Zonal limitations are based on the following:

## Slide 11
Wind Unit Limitations – (S7) Loss of Barilla – Fort Stockton 138kV loads Barilla – Fort Stockton 69kV
Wind Unit Name | Capacity | Limit
SW_MESA_SW_MESA | 75 | 56
WOODWRD1_WOODWRD1 | 83 | 62
INDNNWP_INDNNWP (RRWF) | 83 | 69
INDNENR_INDNENR (RRWF) | 84 | 70
INDNENR_INDNENR_2 (RRWF) | 77 | 65
KING_SW_KINGSW | 79 | 59
KING_NW_KINGNW | 79 | 59
WOODWRD2_WOODWRD2 | 77 | 58
KING_SE_KINGSE | 40 | 30
KING_NE_KINGNE | 79 | 59
Total | 756 | 587
Posted Daily at:
https://tcr.ercot.com/default.cfm?func=tcrpostings
www.ercot.com>
ERCOT TCR Auctions>
Postings/News

## Slide 12: Real Time Contingency Analysis
Runs at regular 5-minute intervals, or upon demand, using the State Estimator Solution and Network Topology.
Identifies areas of congestion, both local and zonal, in post-contingency situations.
  Allows operators to mitigate potential problems before a given contingency occurs (N-1 secure).
  Minimizes the potential for load loss or equipment damage when a contingency does occur.

## Slide 13: Real Time Contingency Analysis

## Slide 14: Zonal Shift Factors
The average effect that changing generation in a zone has on a particular CSC constraint
Zonal Shift Factor S-H
Zone
.19
South
South
100MW
19 MW
-0.16
Houston
Houston
100MW
16 MW
South-Houston CSC

## Slide 15: Average Weighted SF vs Resource SF
CSC
If SPD calculates need for 100 MW to get 16 MW of relief, SPD could get from 11 to 42 MW
Resource/Zone | Shift Factor
W.A. Parish | -.11
Dow | -.42
Houston Zone | -.16

## Slide 16: Building a Zonal Constraint
“Actual Flow” here is actually a SPD calculated flow, not a real time flow value.
Constraint Limit (OC1) is number set by the operator which SPD uses to control the “Actual Flow” (SPD Calculated Flow)

## Slide 17: Resource Shift Factors
Resource shift factor defines the effect that one MW of change in generation (at a specific bus) has on the MW flow on a particular local constraint.
Nueces Bay
Whitepoint
Nueces Bay - Whitepoint
Shift Factor
Generator
0.6
G1
G1
20MW
12 MW
-0.2
G2
G2
20MW
4 MW
Notes: Explain + shift factor means will decrease Nueces bay

## Slide 18: Detail of Local Constraint
Nueces Bay - Whitepoint

## Slide 19: Building a Local Constraint
Resource Names Withheld

## Slide 20: Types of Deployments
Operate at MW level
Based on OC2 Limit and Resource Specific Premium
+ and -
Resource
Local
4
Operate at or above MW level
Based on OC2 Limit and Resource Specific Premium
_
Resource
Local
3
Operate at or below MW level
Based on OC2 Limit and Resource Specific Premium
+
Resource
Local
2
Deliver quantity above or below schedule
Based on Energy Balance, OC1 Limit, and BES Bid Curves
+ or -
Portfolio
Zonal
1
Deployment Instruction
Computation
Shift Factor*
Portfolio/
Resource
Zonal/
Local
Category
* Shift factor is relative to binding Operational Constraint

## Slide 21: Selection Basis
Local Balancing Energy - Deployed by System
  Premium Bids
    Set by Protocols
    Based on Technology Type
  Shift Factors
    Based on power flow studies at peak load by ERCOT Operations Support (engineering) for OC2
    Based on Simultaneous Feasibility Test (SFT) OC3
OOME - Deployed by Operator
  Shift Factors

## Slide 22: CM Action Assessment
Operator must make a decision about what the congestion situation will be 20 minutes into the future, based on observations of
  Current Physical MW flow and difference from Physical MW limit
  Telemetered MW trend
  SPD calculated flows for current and next few intervals relative to OC1 and OC2 limits
Based on this decision, Operator must finalize OC limits 20 minutes beforehand; SPD then executes to produce deployment instructions for interval that starts 20 minutes later
Operator can view deployment results but any adjustments made will impact two intervals in the future.
Any adjustments must also depend on what is observed in the next 15 minute interval
Do I need to activate a constraint?
Notes: NERC violation over N-1 contigency limit for 30 mins

## Slide 23: SPD Calculated Flow
SPD-calculated flow is a value used by the ERCOT Operator in determining how much to adjust constraint limits (OC1, OC2) when activating congestion management
For CSCs, the Calculated Flow is based on Net Generation minus Forecasted Load for each CM zone
  Net Generation is defined as Actual Generation adjusted to reflect (a) where the resource plan does not support the schedules, (b) non-spinning reserve deployments, and (c) balancing awards
  ERCOT Forecasted Load, not Scheduled Load, is used as the load component
  Shift factors are applied to the above for each CSC zone to arrive at the SPD Calculated Flow for the CSC
SPD CF is what SPD uses to represent the MW loading on a CSC
SPD CF is not available for view by Market Participants

## Slide 24: OC1 and Physical Limit Review
SPD OC1 don’t normally match Physical limits on CSC/CRE Data Display
SPD predicts congestion and responds with congestion control based on calculated flows that may bear little resemblance to Physical MW flows that actually occur
SPD computes optimum deployment based on entered OC limits relative to SPD calculated flow
ERCOT Operator activates congestion management based on the predicted effect on Physical MW flow relative to its Physical Limit, by adjusting the OC limit relative to the SPD Calculated Flow
Notes: Go back to moi slide if nec to show flow.

## Slide 25: Local Congestion
Local congestion is non-CSC congestion
ERCOT Operator monitors post-contingency physical MW flow against physical limits set by TO
SPD limits for these elements are called OC2 limits
Deployment on individual resource basis as opposed to portfolio-of-resources basis
ERCOT Local CM “tools” are all “net zero” within a zone
Deployment instruction can be
  Category 2 (at or below),
  Category 3 (at or above), or
  Category 4 (to a level)
In addition, Operator may manually direct units to specific MW levels (OOME)
OOME directive can be deployed effective immediately rather than 2nd-to-next 15 minute interval
Works essentially the same as zonal congestion previously discussed, except as follows
There are no portal displays for viewing local congestion situations or status

## Slide 26: Real Time Contingency Analysis
RTCA
  Runs every 5 minutes
  Performs contingency analysis on over 2000 contingencies
  Ensures power system is operating in a secure state
  Constraints on market minimized to those times when a contingency overload would otherwise occur.

## Slide 27: Simultaneous Feasibility Test
Prevents physical operating limits from being exceeded by constraining the optimized SPD solution during:
  Realtime Redispatch 14 min before start of each Interval (9 minutes before ramp starts)
Constraint Examples:
Lines at rated normal MVA loading with no contingencies
Lines at rated emergency limits during contingency outages

## Slide 28: PCAPs
Pre-Contingency Action Plans are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability.

## Slide 29: Remedial Action Plans (RAPs)
Designed to relieve the loading on a Transmission Facility within 15 minutes.
ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the 15-Minute Rating.
The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, the Emergency Rating within 15 minutes.
Remedial Action Plans are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions.

## Slide 30: Mitigation Plans (MPs)
Pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload.
With a Mitigation Plan, an operator does not need to declare an alert for a post contingency overload.
Mitigation Plans are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions.

## Slide 31
CSC Name
Labeled fields the same data as shown on CSC/CRE Data Web Display
2
2. Summed Physical MW flow
3
3. Summed Physical MVAR flow
4
4. Manually-entered Physical MW post contingency limit (Calculated Daily by Engineering)
1
Real-Time Data Web Display

## Slide 32
MW Scheduled Impact = [Scheduled Generation - Scheduled Load] x [Monthly Shift Factor] for each CM zone
The MW Scheduled Impact (SI) for each CM Zone is summed for a particular CSC to arrive at the Total MW Scheduled Impact on the particular CSC
Market Participants can view SI values but these values are not used by the ERCOT Operator
A calculated quantity that reflects the predicted MW flow for a particular CSC based on schedules
MW Scheduled Impact (SI)
Notes: SI is:
Calculated only for CSCs
based on monthly zonal SFs
Direct Assignment of Zonal congestion costs is based on each QSEs SI on each constraint
CSC congestion charge = SP of CSC * SI
IF THE SI EXCEEDS THE MONTHLY OC0---is it the case that TCRS may not fully hedge your transactions….???(pamela)

## Slide 33
Selectable date
Selectable hour
Selectable interval
Abbreviated CSC Name
OC0 Limit for each CSC
OC1 Limit for each CSC used as input into SPD
CM zone name
Monthly zonal shift factor *
MW Scheduled Impact (SI)
Total SI
Shadow price
4
5
6
1
2
3
7
8
9
10
11
* This represents expectations from a power flow case done the month ahead
CSC Web Display
Notes: QSEs schedule Resources and Oblig by zone, sched do not need to be balanced (for QSEs with load)
Sched Impact * SP = Direct Assignment of Congestion costs

## Slide 34
Shows data three days into the past and for remainder of today and tomorrow
OC1 shows current market constraint
  Manually updated in the adjustment or operating period as needed
OC1 < 9999 does not necessarily indicate that there will be a zonal congestion charge (shadow price)
Shadow Price > $0.0 is indication that zonal congestion is being relieved with Balancing Energy
No information provided about local congestion
More About the CSC Display
Notes: T-14 is when balancing deploys—was changed from T-20 in July 2003

## Slide 35
Congestion Management Review Questions
1. What ERCOT software determines the optimal balancing instructions to relieve congestion?
a) OOM
b) SPD
c) EMS
d) EECP

## Slide 36
Congestion Management Review Questions
2. How many CSC zones abide in ERCOT?
a) 3
b) 4
c) 5
d) 6

## Slide 37
Congestion Management Review Questions
3. Local congestion is controlled with
a) inter-zonal portfolios
b) non-zero shadow pricing
c) N-1 security criteria
d) resource-specific deployment

## Slide 38
Congestion Management Review Questions
4. SPD executes every ___ minutes to deploy Balancing Energy.
a) 15
b) 30
c) 45
d) 60

## Slide 39
Congestion Management Review Questions
5. SPD’s OC3 constraint is an automatically created limit applied locally in real-time.
a) True
b) False

## Slide 40
Congestion Management Review Questions
6. Real-Time Contingency Analysis runs
a) at regular 5-minute intervals
b) upon demand
c) both a and b
d) neither a nor b

## Slide 41
Congestion Management Review Questions
7. The following setting indicates a constraint is not active:
a) 0000
b) Z9A1
c) 9999
d) N/A

## Slide 42
Congestion Management Review Questions
8. A Category 1 deployment instructs
a) a local resource to operate at MW level
b) a local resource to operate at or above MW level
c) a local resource to operate at or below MW level
d) a zonal portfolio to deliver quantity above or below schedule

## Slide 43
Congestion Management Review Questions
9. OOME is deployed by
a) the System
b) the PUC
c) the Operator
d) the ERCOT Board

## Slide 44
Congestion Management Review Questions
10. SPD Calculated Flow is available for view by Market Participants.
a) True
b) False

## Slide 45
Congestion Management Review Questions
11. SFT calculates
a) shift factors
b) incremental costs
c) line losses
d) power flow

## Slide 46
Congestion Management Review Questions
12. Remedial Action Plans and Mitigation Plans are
a) contingency definitions for performing power flow analysis
b) designed to be enacted pre-contingency
c) performed hourly
d) designed to be enacted post-contingency