## Slide 1
GET READY FOR SUMMER March 10, 2005
Kenneth A. Donohoo, PE
Manager of System Planning
Transmission Services

## Slide 2
The National Grid Of Texas

## Slide 3
Wind Generation In ERCOT
1,300 MW of wind generation has been added since 2001
Most of the wind generation has been built in West Texas where there was insufficient transmission in place to get the power to load centers
The Texas Energy Council has recommended up to 3,000 MW more be added to the State’s goals
  Additional transmission will be required
  More information is needed on the impact of wind diversity and the impact on other forms of generation
  Voltage control issues must be resolved

## Slide 4
Total 2127 MW
In-service &
Under Development
Wind Locations

## Slide 5: Transmission Planning Process
  Projects or studies can be proposed by any Market Participant, Transmission Owner or ERCOT Staff
  Stakeholders have opportunity to comment on proposals and offer alternative solutions
  ERCOT Staff performs independent review
  ERCOT Staff makes independent recommendation to the Board of Directors for major projects
  ERCOT Board determines whether project will receive ERCOT endorsement based on Staff recommendation
ERCOT has implemented an open and non-discriminatory planning process that considers and balances the impacts of transmission facility additions on stakeholders

## Slide 6: Regional Planning Groups
ERCOT leads and facilitates three Regional Transmission Planning Groups (North, South and West)
The groups are open to all ERCOT stakeholders
Information about planned transmission projects is distributed to and among members of these groups
These groups provide the means for stakeholders to participate, express concerns, share alternatives, and provide input to the ERCOT staff independent recommendation

## Slide 7: Implementation of New Transmission Projects
The ERCOT Planning Process is only one part of a broader process through which new transmission is implemented
Notes: <number>
The ERCOT Planning Process is only one part of a broader process through which new transmission is implemented
Turquoise boxes show steps in implementation process and the blue boxes show who is responsible for each step.
Will talk about ERCOT Planning Process box in detail on next slide.
Note that time frame from the identification of need until project construction may be 5-6 years.
Note that PUCT participates in ERCOT planning process, has authority over CCN approval and determines whether the project is put into rate base.

## Slide 8: Implementation of New Transmission Projects
Project development and review
Regulatory review
Notes: <number>
The ERCOT Planning Process is only one part of a broader process through which new transmission is implemented
Turquoise boxes show steps in implementation process and the blue boxes show who is responsible for each step.
Will talk about ERCOT Planning Process box in detail on next slide.
Note that time frame from the identification of need until project construction may be 5-6 years.
Note that PUCT participates in ERCOT planning process, has authority over CCN approval and determines whether the project is put into rate base.

## Slide 9: Implementation of New Transmission Projects
Construction
Notes: <number>
The ERCOT Planning Process is only one part of a broader process through which new transmission is implemented
Turquoise boxes show steps in implementation process and the blue boxes show who is responsible for each step.
Will talk about ERCOT Planning Process box in detail on next slide.
Note that time frame from the identification of need until project construction may be 5-6 years.
Note that PUCT participates in ERCOT planning process, has authority over CCN approval and determines whether the project is put into rate base.

## Slide 10: Planning Process Results
  Facilities added and currently in-service
    26,500 MW of generation capacity (over 45% increase) interconnected
    Nearly $2 billion invested in transmission facilities
    700 miles of new 345 kV transmission lines
    Several hundred miles of new or rebuilt 138 kV transmission lines
    Many 345/138 kV transformers
    Dynamic and static voltage control devices
  Underway
    619 miles 345 kV transmission lines
    Many 138 kV lines and upgrades
    Additional $1.8 billion will be invested in the transmission system, based on current projections
  Much greater expansion of transmission infrastructure than in any other region of North America

## Slide 11
Major Transmission Completed

## Slide 12
Endorsed & Projects Understudy

## Slide 13: Current ERCOT Reserve Margin Projection
Year | 2005 | 2006 | 2007
ERCOT-approved definition | 16.6% | 28.9% | 25.9%
If TxGenCo were retired | 14.0% | 22.9% | 20.0%
Excluding mothball plants unlikely to return | 14.0% | 11.8% | 10.9%
Current ERCOT reserve requirement is 12.5%

## Slide 14: Planning Criteria
ERCOT Planning Criteria state the fundamental minimum requirements for planning and constructing reliable interconnected electric systems under:
  Normal Condition
    PC Category A
  Single Contingency Conditions
    PC Category B
    Includes the contingency loss of single faults resulting in multiple elements (SFME) out
    Includes the contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length
      Double circuit = Single contingency = Category B
    Includes the contingency loss of any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element
      Generator + Single contingency = Category B
  Multiple contingency conditions
    PC Category C & D
    Allows generation, load and/or system adjustment

## Slide 15: PLANNING CRITERIA Category B
The contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans), such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.
2. With any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the transmission element, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans) such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.
Generator + Single contingency = Category B
Double circuit = Single contingency = Category B

## Slide 16: PLANNING CRITERIA
Voltage stability margin shall be sufficient to maintain post-transient voltage stability within a defined importing (Load) area under the following study conditions:
  Peak Load conditions, with import to the area increased by five percent (5%) of the forecasted area Load, and NERC Category A or B operating conditions (see NERC Table I in ERCOT Planning Criteria); and
  Peak Load conditions, with import to the area increased by two and one half percent (2.5%) of the forecasted area Load, and NERC Category C operating conditions.

## Slide 17: Automatic Under Voltage Load Shed
In-Service
Under Review
Lower Rio Grande Valley – 25% of load
Laredo – 25% of load
Houston – 25% of load
DFW – 10% of load developing to 25%

## Slide 18: Get Ready
Long Range Weather Forecast (NOAA)
  Rainfall normal
  Normal temperatures in North Texas
  Above normal temperatures in South and West Texas
Peak Demand Projection 59,800 MW
System Protection Review of Critical Facilities
Communications Ready
Improve System Modeling and Data Exchange
Increase Training and Coordination
  Real-Time Operating Tools and Information
  System Restoration
  Reevaluate Operating Criteria
Increase Operational Awareness
  Act, notify and document when something does not feel or appear “right”

## Slide 19: Get Ready
Reactive Power and Voltage Control
  Load Serving Entities
    Capacitors functional and available for operation
  Transmission Owners/Operators
    Capacitors functional, available and operated early
  Generation Owners/Operators
    Generator cooling, testing and operator training complete/ready by May 1
    Generator must operate in voltage control mode not power factor mode
    Operating and maintaining correct voltage schedule
    Fully responsive to voltage changes and must ride through voltage excursions
    All reactive or voltage limitations or changes must be communicated to ERCOT Operations via QSE
    Critical areas for voltage control
      Dallas-Fort Worth
      Houston
      Laredo
      Lower Rio Grande Valley
      West Texas

## Slide 20
Future Issues
Stability (transient and voltage) limits becoming major limitation rather than thermal limits
  Development of software stability models problematic
  Validation/testing is also problematic
Shrinking generation reserve margins as a result of old, less efficient units being shut down
Dual fuel or reserve fuel for the growing amount of natural gas generation
Nodal versus zonal markets
Power quality
  Once the role of the bundled utility
  Who has responsibility in the unbundled world?