## Slide 1: Operational Issues
Presented by: John Adams

## Slide 2: Agenda
Northeast Blackout Review
List of Critical failures leading to event
Review of NERC Recommendations
ERCOT Response to Recommendations
Voltage Stability Analysis Review
Description of SOL’s and IROL’s
Description of Dynamic Ratings

## Slide 3: Northeast Blackout Review
On August 14, 2003, the Midwest, the Northeast United States and Ontario, Canada, experienced an electric power blackout.
The outage affected an estimated 50 million people and 61,800 megawatts (MW) of electric load.
States affected:
  Ohio Michigan
  Pennsylvania New York
  Vermont Massachusetts
  Connecticut New Jersey
  Ontario, Canada

## Slide 4: Northeast Blackout Review Cont.
Estimates of total costs in the United States range between $4 billion and $10 billion
In Canada there was a net loss of 18.9 million work hours, and manufacturing shipments in Ontario were down $2.3 billion (Canadian dollars).

## Slide 5: NERC Identified Causes of Blackout
Inadequate Tree Trimming
  Overgrown trees caused Harding-Chamberlain 345 kV trip @ 43.5% of normal/emergency rating
  Overgrown tree caused Hanna-Juniper 345 kV trip at 87.5% of normal/emergency rating
  Overgrown tree caused Star-South Canton 345 kV trip at 93.2% of normal/emergency rating

## Slide 6: NERC Identified Causes of Blackout
Inadequate Reliability Coordinator Diagnostic Support
  Reliability Organization had no real time data from Dayton P&L Stuart-Atlanta 345 kV line incorporated into its State Estimator. This prevented MISO becoming aware of FE system problems
  Reliability Organization was using non-real time data to support “flowgate” monitoring.
  Reliability Organization had no effective means of identifying location and significance of transmission line Breaker operations
  PJM and MISO lacked joint procedures on when and how to coordinate

## Slide 7: NERC Identified Causes of Blackout
Inadequate Situational Awareness
  No effective Contingency Analysis Capability
  No procedure to be sure operator aware of state of functional modeling tools
  No procedure to test tools after repairs
  Insufficient tools for high level monitoring
Inadequate Tree Trimming
Inadequate RC Diagnostic Support

## Slide 8: List of NERC Conclusions
From its investigation of the August 14 blackout, NERC concludes that:
  Several entities violated NERC operating policies and planning standards, and those violations contributed directly to the start of the cascading blackout.
  The existing process for monitoring and assuring compliance with NERC and regional reliability standards was shown to be inadequate to identify and resolve specific compliance violations before those violations led to a cascading blackout.
  In some regions, data used to model loads and generators were inaccurate due to a lack of verification through benchmarking with actual system data and field testing.

## Slide 9: List of NERC Conclusions
  Reliability coordinators and control areas have adopted differing interpretations of the functions, responsibilities, authorities, and capabilities needed to operate a reliable power system.
  Problems identified in studies of prior large-scale blackouts were repeated, including deficiencies in vegetation management, operator training, and tools to help operators better visualize system conditions.
  Planning studies, design assumptions, and facilities ratings were not consistently shared and were not subject to adequate peer review among operating entities and regions

## Slide 10: List of NERC Conclusions
  Planning studies, design assumptions, and facilities ratings were not consistently shared and were not subject to adequate peer review among operating entities and regions.
  Available system protection technologies were not consistently applied to optimize the ability to slow or stop an uncontrolled cascading failure of the power system.

## Slide 11: NERC Recommendations
  Correct the Direct Causes for the August 14, 2003 Blackout
  Strengthen the NERC Compliance Enforcement Program
    Require Significant Violations/ Quarterly Violations Reporting – within 1 Month
    Require Organizations to correct violations
    Develop Compliance Templates
    NERC compliance Enforcement within 3 months issue final report.
  Initiate Control Area and Reliability Coordinator Reliability Readiness Audits
    Establish Readiness Audits program
    Set baseline audit criteria
    Audit each control area with oversight and participation of NERC.
  Evaluate Vegetation Management Procedures and Results
    Initiate Vegetation Related Outage Reporting Program
    Each TO submit annual Vegetation Related Outages
    Each TO make available Vegetation Management Procedures and documentation

## Slide 12: NERC Recommendations
  Establish a Program to Track Implementation of Recommendations
    Recommendations Actions Tracking Program
    Establish Reliability Performance monitoring function
  Improve Operator and Reliability Coordinator Training
    Operators Training minimum 5 days/year on system emergencies.
  Evaluate Reactive Power and Voltage Control Practices
    Planning Committee reevaluate within 1 year effectiveness
    ECAR review reactive power and voltage criteria and procedures.
  Improve System Protection to Slow or Limit the Spread of Future Cascading Outages
    Zone 3 Relay Review/Analysis
    UVLS Studies within 1 year
    NERC Planning Committee evaluate planning Standard III
  Clarify Reliability Coordinator and Control Area Functions, Responsibilities, Capabilities and Authorities

## Slide 13: NERC Recommendations
  Establish Guidelines for Real-Time Operating Tools
  Evaluate Lessons Learned During System Restoration
    Blackstart & Restoration Evaluation of NPCC, ECAR, PJM
  Install Additional Time-Synchronized Recording Devices as Needed
    Regional Criteria for Synchronized Recording Devices
    Dynamic Recorder Upgrade/Installation
  Reevaluate System Design, Planning and Operating Criteria
    Operating Committee evaluate planning and operating criteria
    ECAR reevaluate study procedures and practices
    Planning committee reevaluate criteria, methods, and practice for design, planning and analysis.
  Improve System Modeling Data and Data Exchange Practices
    Model Data Validation

## Slide 14: ERCOT’s Response to Recommendations
Strengthen the NERC Compliance Enforcement Program
  ERCOT compliance has implemented 48 hour reporting of significant reporting violations
  No action required until violation reported.
  NERC Board approved 37 templates for 2004, mostly revisions to existing measure
  NA to ERCOT (ECAR)
Initiate Control Area and Reliability Coordinator Reliability Readiness Audits
  NERC has scheduled a readiness audit for ERCOT in October 2005

## Slide 15: ERCOT’s Response to Recommendations
Evaluate Vegetation Management Procedures and Results
  A NERC compliance measure has been approved, ERCOT guides have be revised to require monthly reporting.
  ERCOT has received monthly reports from TO’s. ERCOT will file annual report by 3/31/2005
  ERCOT transmission companies provided plans to ERCOT as part of submittal. ERCOT compliance includes review as part of annual self-certification.
Establish a Program to Track Implementation of Recommendations
  ERCOT compliance created a database to track recommendations and other issues.

## Slide 16: ERCOT’s Response to Recommendations
Improve Operator and Reliability Coordinator Training
  All 345kv Owners met this recommendation by June 30 2004. Training requirement added to operating guides.
NERC re-evaluation – NA to ERCOT at this time
Improve System Protection
  Zone 3 relay review - All ERCOT 345kv Owners met this recommendation.
  Evaluate under voltage relaying – Installations in Houston and DFW
  NERC review of Planning Standard III. NA to regions.

## Slide 17: ERCOT’s Response to Recommendations
Evaluate Lessons Learned During System Restoration
  In hands of NERC at this time
NERC Operating Committee review Real time Operating tool
NERC Planning Committee evaluate restoration
Install Additional Time-Synchronized Recording Devices as Needed
  ROS revised Operating Guides to define locations that need time synchronization and evaluate whether enough time synced equipment is installed
  ERCOT Dynamics Wording group has defined an annual review process for location of dynamic Disturbance recorders. 1st review should complete February 2005.
Reevaluate System Design, Planning & Operating Criteria – All NERC
Improve System Modeling Data and Data Exchange Practices
  ROS assigned DWG to define what should be done here for modeling data and simulations, beyond any current validation.

## Slide 18: Voltage Stability Analysis
Checks voltage range violation, voltage stability, and overload violations for current operating point.
Calculates transfer limit based on voltage and overload criteria.
Prevents ERCOT grid from entering an insecure state in which an individual contingency could lead to voltage collapse (instability) situation.

## Slide 19: Voltage Stability Analysis Cont.
Study Network Sequence (STNET) and Dynamic Case Preparation (DCP) are used to define and validate VSAT case files.

## Slide 20: ERCOT VSAT
ERCOT operations engineers create a power flow case describing the highest stress period on the power system.
Based on this valid power flow case, a VSA study is performed, in which a set of scenarios and contingency groups are analyzed.
If the VSA interface limit is smaller than the corresponding thermal limit, set VSA interface limit as daily limit.

## Slide 21: System Operating Limits
System Operating Limit (SOL)
  The value that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria.
  MW, MVar, Amperes, Frequency, or Volts
Operating criteria:
  Facility Ratings
  Transient Stability Limits
  Voltage Stability Limits
  System Voltage Limits

## Slide 22: Interconnected Reliability Operation Limits
Interconnected Reliability Operating Limit (IROL)
  The value derived from, or a subset of, the System Operating Limits, which if exceeded, could expose a widespread area of the bulk electrical system to instability, uncontrolled separations or cascading outages.
  MW, MVar, Amperes, Frequency, or Volts

## Slide 23: Dynamic Ratings
Dynamically rating transmission elements is based on at least ambient temperature to reflect the actual conditions rather then the worst expected conditions
  Ratings may be delivered via ICCP from Transmission Service Provider
  These ratings can be either in AMP or in MVA
  Transmission Service Provider can send the ratings by weather zone temperature
  Used to determine ratings based on a look up table between line vs temperatures

## Slide 24: Dynamic Ratings
Transmission facilities are typically:
  Rated assuming a high ambient temperature for summer
  Rated assuming a low ambient temperature for winter
  Conservative values for each
Suggests that additional transmission capacity is often available if the actual ambient temperature or convection is known .
Transmission Providers may wish to provide “dynamic” ratings, which are based on more than temperature changes

## Slide 25: Dynamic Ratings Impact
Most of the ERCOT transmission line ratings were set at 98F or 104F.
Historical data shows that 80% of the time the ambient temperatures in Texas are below 95F.
The average temperature is around 60F.
Dynamically rated the transmission lines will increase the existing transmission capacity .

## Slide 26: Constraint Activity Manager
CAM acts between RTCA and SPD in calculating amount of balancing energy to deploy to allow operator to enable constraints, calculates shift factors, and passes information on state of current system.

## Slide 27
Local Constraint Flowchart For Each Interval
State Estimator Solution With Current Network Topology / Loads
Power Flow Case with Network Topology and MW Injections
SPD
SFT Loadflow with
Contingency Analysis
Generates Limited Unit Specific Constraints
Optimized
Constrained
Dispatch for the Interval
Current System
Manually Entered Constraints (oc2)
QSE/CMZ Res. Plan & Real-Time Outputs
QSE Schedules and Bid (inc. BES)
Addition of CAM/SFT to Process
Iterate Once
RTCA
Basecase/Cont Overload Detect
CAM
Basecase/Contingency Overloads Selectable for Deploy
Old

## Slide 28: Constraint Activity Manager

## Slide 29: Release 4 – June 2005
1 – Simultaneous AS Allocation
2 – Resource Plan Improvements
3 – Resource Specific Bid Limits
4 – RPRS Market Redesign
5 – Simultaneous Selection of AS
6 – PUCT Config File Tracking and Archiving
7 – OOM Tool Enhancements
8 – SFT Enhancements
9 - VSA/DSA improvements

## Slide 30: Operational Issues
1. From its investigation of the August 14, Blackout, NERC concludes that:
Several entities violated _____ operating policies and planning standards, and those violations contributed directly to the start of the cascading blackout.
a. ERCOT
b. NERC
c. FERC
d. SPP

## Slide 31: Operational Issues
2. From its investigation of the August 14 blackout, NERC concludes that:
In some regions, data used to model loads and generators were inaccurate due to a lack of verification through benchmarking with actual system data and field testing.
True/False

## Slide 32: Operational Issues
3. From its investigation of the August 14 blackout, NERC concludes that:
Problems identified in studies of prior large-scale blackouts were _____, including deficiencies in _____ management, operator training, and tools to help operators better visualize system conditions.
a. repeated, upper
b. repeated, vegetation
c. not repeated, vegetation
d. none of the above

## Slide 33: Operational Issues
4. Which of the following is not a NERC recommendation in reference to the August 14 Blackout
a. Strengthen the NERC Compliance Enforcement Program
b. Initiate Control Area and Reliability Coordinator Reliability Readiness Audits
c. Evaluate Vegetation Management Procedures and Results
d. Violate NERC operating policies and planning standards

## Slide 34: Operational Issues
5. System Operating Limit (SOL) is the value that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria.
True/False

## Slide 35: Operational Issues
6. Interconnected Reliability Operating Limit (IROL) and System Operating Limit (SOL) are measured by…
a. MW
b. MVar, Amperes
c. Frequency or Volts
d. All of the above

## Slide 36: Operational Issues
7. Most of the ERCOT transmission line ratings are set at ____ or ____ ambient air temperature.
a. 98ºF or 104ºF
b. 95ºC or 105ºC
c. 32ºF or 42ºF
d. none of the above

## Slide 37: Operational Issues
8. Historical data shows that 80% of the time the ambient temperatures in Texas are below ___F. The average temperature is around ___F.
a. 95, 60
b. 32, 60
c. 45, 32
d. 70, 70

## Slide 38: Operational Issues
9. Which of the following states was not affected by the Northeast blackout.
a. Ohio
b. Washington
c. Michigan
d. New York

## Slide 39: Operational Issues
10. All of the following resulted from the Northeast Blackout except…
a. 50 million customers affected
b. 61,800 mw of electric load dropped
c. parts of Canada Profited
d. parts of Canada Blacked out

## Slide 40: Operational Issues
Now for your Questions ?