## Slide 1
ERCOT Frequency Control
Sydney L. Niemeyer

## Slide 2
Introduction
ERCOT Frequency Control is intended to refresh your understanding of frequency limits of the interconnection and the tools available to ERCOT to Balance Resources and Demand.

## Slide 3
Objectives
At the completion of this course of instruction you will:
recognize Frequency limits of the ERCOT interconnection
be able to describe how ERCOT maintains frequency to meet the NERC Control Performance Standard

## Slide 4
Definitions
1 DCS - The Disturbance Control Standard measures the Control Area’s ability to utilize its Contingency Reserves following a Reportable Disturbance.
2 AGC – Automatic Generation Control – The QSE control system that automatically changes output of resources in response to ERCOT electronic instructions.

## Slide 5
Content
Frequency Operating Limits
NERC Control Performance Standard
Ancillary Services to meet the NERC Control Performance Standard

## Slide 6: Automatic Firm Load Shed
60.00
59.00
57.00
61.00
62.00
63.00
58.00
3420
3480
3540
3780
3720
3660
3600
1890
1860
1830
1710
1800
1740
1770
4 Pole
2 Pole
Generator RPM
58.5 Hz 10% Firm Load Shed
58.9 Hz 10% Firm Load Shed
59.3 Hz 5% Firm Load Shed
The frequency measuring relays shall have a time delay of no more than 30 cycles (or 0.5 seconds for relays that do not count cycles). If the frequency and time values are reached, an irretrievable trip is initiated. Total time from the time when frequency first reaches one of the values specified below to the time load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.
Hz
Notes: At ERCOT minimum load conditions, typically 22,000 MWs, 5% load shed is 1100 MW. 10% load shed is 2200 MW. At ERCOT peak load of 61,000 MW, 5% load shed is 3050 MW. 10% load shed is 6100 MW. The loads that actually trip at each setting could be slightly higher or lower than these values.

## Slide 7: Typical Frequency Limits
60.00
59.00
57.00
61.00
62.00
63.00
58.00
3420
3480
3540
3780
3720
3660
3600
1890
1860
1830
1710
1800
1740
1770
4 Pole
2 Pole
Generator RPM
Combustion Turbines
57.6 Hz Trip after 60 seconds
56.5 Hz Trip after 20 seconds
63.3 Hz Trip after 1.5 seconds
62.3 Hz Trip after 60 seconds
Hz
Notes: Different manufacturers have different Trip set-points. These are typical. Your set-points may be different, but should not be prior to Automatic Firm Load Shed.

## Slide 8: Typical Frequency Limits
60.00
59.00
57.00
61.00
62.00
63.00
58.00
3420
3480
3540
3780
3720
3660
3600
1890
1860
1830
1710
1800
1740
1770
4 Pole
2 Pole
Generator RPM
Steam Turbines
5% & 10% or 63 & 66 Hz Over speed Trip
62.5 Hz Trip Immediately
62.0 Hz Trip after 2 seconds
61.6 Hz Trip after 30 seconds
60.6 Hz Trip after 9 minutes
59.4 Hz Trip after 9 minutes
58.4 Hz Trip after 30 seconds
58.0 Hz Trip after 2 seconds
57.5 Hz Trip Immediately
Continuous Operation Range
Hz

## Slide 9: Typical Frequency Limits
60.00
59.00
57.00
61.00
62.00
63.00
58.00
3420
3480
3540
3780
3720
3660
3600
1890
1860
1830
1710
1800
1740
1770
4 Pole
2 Pole
Generator RPM
Steam Turbines some Manufacturers
5% & 10% or 63 & 66 Hz Over speed Trip
63.0 Hz Trip Immediately
57.9 Hz Trip after 108 seconds
57.4 Hz Trip after 15 seconds
56.9 Hz Trip after 2.4 seconds
Continuous Operation Range
Hz

## Slide 10: ERCOT Control Performance Limits
60.00
59.95
59.85
60.05
60.10
60.15
59.90
3591
3594
3597
3609
3606
3603
3600
1804.5
1803
1801.5
1795.5
1800
1797
1798.5
4 Pole
2 Pole
Generator RPM
60.03 Hz one minute average High Limit
59.97 Hz one minute average Low Limit

## Slide 11: NERC Control Performance Standard
CPS1
CPS1 = 100 or higher (passing)
The NERC Control Performance Standard (CPS) establishes the statistical boundaries for ACE magnitudes, ensuring that steady-state frequency is statistically bounded around its scheduled value.
Notes: ERCOT CPS1 = {2 – [(Hz dev) x (Hz dev)]/(0.03 x 0.03)} x 100 Note: Hz dev is 1 minute average, averaged over the month. 12 month rolling average must remain 100.0 or above to pass. December 2004 12 month rolling average for ERCOT was 127.23. ERCOT has a waiver on CPS2.

## Slide 12: ERCOT CPS1
If ERCOT’s 1 minute average frequency is 59.98 Hz, their CPS1 score for the minute is 155.56
Notes: The graph is drawn with scheduled frequency at 60.00 Hz. If ERCOT is in a time correction, scheduled frequency at 59.98 or 60.02 Hz, the graph will shift to the left or right to compensate.

## Slide 13: Purpose of Responsive Reserves
NERC Policy 1 – Generation Control and Performance
  B. Disturbance Control Standard
    Each Control Area shall have access to and/or operate resources to provide for a level of Contingency Reserve sufficient to meet the DCS performance standards.
Notes: Compliance is met when the Control Area returns its ACE (frequency in ERCOT) to schedule or to pre-disturbance values within the DISTURBANCE RECOVERY PERIOD when it experiences a REPORTABLE DISTURBANCE. In ERCOT a reportable event is the loss of resources between 1000 and 1250 MWs and the Recovery period is 15 minutes. ERCOT must meet this standard 100% of the time to be compliant.

## Slide 14: Responsive Reserve from Resources
Operating reserves ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency.
  Responsive Reserve deploys automatically through governor action
  Deployed for the Operating Hour in response to loss-of-Resource contingencies on the ERCOT System.
Notes: Frequency will deploy Responsive Reserve on generators through governor action at the rate of 191.67 MW/0.1 Hz. 1150 MW on generators at 5% droop will consume all responsive reserve at 59.40 Hz

## Slide 15: Sources of Responsive Reserve
Unloaded Generation Resources that are On-line
Resources controlled by high set under-frequency relays
Hydro Responsive Reserve
Direct Current (DC) tie-line response. The DC tie-line response must be fully deployed within fifteen (15) seconds on the ERCOT System after the under frequency event

## Slide 16: Responsive Reserve Service
ERCOT procures 2300MW of Responsive Service each operating hour
  1150 must be supplied by synchronized generation resources
    Generators, hydro & DC ties
  Up to 1150 MW may be procured from Load acting as a Resource (LaaR)

## Slide 17: Load Acting as a Resource
60.00
59.90
59.70
60.10
60.20
60.30
59.80
3582
3588
3594
3618
3612
3606
3600
1809
1806
1803
1791
1800
1794
1797
4 Pole
2 Pole
Generator RPM
Maximum of 1150 MW allowed
59.8 Hz One Block of ~160 MW of LaaR Trip
59.7 Hz remaining Block of up to ~990 MW of LaaR Trip
Hz
 Be capable of interruption by automatic operation of the under-frequency relay(s) set to initiate the interruption whenever system frequency reaches a specific value. The initiation setting of the relay shall not be any lower than 59.7 Hz.;
 Be capable of interruption within 20 cycles of the time that frequency decays to a value low enough to initiate action of the under-frequency relay(s);
Notes: The first Block of LaaRs tripping at 59.80 Hz is not required to trip at 59.90 Hz. The tripping frequency cannot be below 59.70 Hz.

## Slide 18: Responsive Reserve Deployment
Interconnection frequency below 59.91 Hz will deploy Responsive Service to QSE’s that represent generators.
The amount of deployment depends on frequency and ERCOT Frequency bias setting
  RR Deployment = -10 x Frequency bias x (Actual Frequency – Recall Frequency) x (Responsive Reserve Request %/100)
Notes: ERCOT frequency bias setting is 604 MW/0.1hz between May 1 and Sep 30 and 533 MW/0.1hz between Oct 1 and April 30. These settings are subject to change. The Recall Frequency is 59.97 Hz. The Responsive Reserve Request % is 67% but can change with ERCOT’s bias setting.

## Slide 19: Primary Frequency Control
Turbine governor droop provides quick response and “resists” frequency change caused by Resource and Demand imbalance.
  Governor droop will not restore system frequency, but will stabilize frequency at some new frequency.
    If generation is higher than the demand this frequency will be above schedule.
    If generation is lower than demand this frequency will be below schedule.
  The more turbines that have an operating governor, the more resistive to change will be the interconnects frequency. This resistance to change is measured by the interconnects Bias setting in MW/0.1 Hz.
Notes: Turbines should have a droop characteristic of 4% or 5% with a maximum dead band of +/-0.036 Hz. A 5% droop characteristic will change a turbines output 100% for a 5% (3.0 Hz) change in frequency. A 4% droop characteristic will change a turbines output 100% for a 4% (2.4 Hz) change in frequency.

## Slide 23: Balancing Energy Deployment
Balancing Energy is deployed for frequency control to maintain Regulation Service near zero net energy each interval.
Base Energy Schedules do not match actual energy demand. Balancing energy provides intra-hour deployments to coarsely maintain frequency on schedule.

## Slide 24: Balancing Resources and Demand

## Slide 25: Regulation Service
Regulation Service is deployed every 2 seconds to Regulation providers to balance Resources to Demand.
  QSE’s awarded Regulation service respond to ERCOT deployments using Automatic Generation Control (AGC) to maintain frequency on schedule.
  QSE’s providing Regulation Service must meet Control Performance Standard similar to CPS1 and CPS2, one and ten minute SCE control standard.
Notes: Regulation Service Providers must report Energy Management/Generation Control System outages to the ERCOT Frequency Desk.

## Slide 26: QSE SCPS1 Score at 59.98 Hz
Score = 100 at SCE = -24 MW
Score = 100 at SCE = -12 MW
Notes: ERCOT Scheduled Frequency of 60.00 Hz. For Regulation Service Providers, their “Monthly average” SCPS1 score must average 100.0 or greater to pass the SCPS1 performance measure.

## Slide 27: QSE SCPS1 Score at 59.96 Hz
Score = 100 at SCE = -12 MW
Score = 100 at SCE = -6 MW
Notes: ERCOT Scheduled Frequency of 60.00 Hz. For Regulation Service Providers, their “Monthly average” SCPS1 score must average 100.0 or greater to pass the SCPS1 performance measure.

## Slide 28: QSE SCPS1 Score at 59.94 Hz
Score = 100 at SCE = -8 MW
Score = 100 at SCE = -4 MW
Notes: ERCOT Scheduled Frequency of 60.00 Hz. For Regulation Service Providers, their “Monthly average” SCPS1 score must average 100.0 or greater to pass the SCPS1 performance measure.

## Slide 29: QSE SCPS2 SCE 10 Minute Limit
The minimum participation factor used is 1% which results in a minimum limit of 9.367 MW
Notes: For each hour a QSE participates in Regulation Service, there are 6 10-minute periods. The QSE’s 10 minute average SCE must be less than the 10 minute limit to pass the period. The QSE must pass 90.0% or above of the 10 minute periods in a month to pass SCPS2. This curve will change when ERCOT changes their Bias setting. Curve based on ERCOT Bias setting of 533 MW/0.1 Hz.

## Slide 30: ERCOT Load and Frequency
Notes: ERCOT Demand is sensitive to changes in frequency and provides some assistance in stabilizing frequency.

## Slide 31: Regulation and Responsive Deployments
Notes: Responsive is deployed at 59.910 Hz and is recalled when frequency returns to 59.970 Hz. Regulation is deployed every two seconds to maintain frequency at schedule.

## Slide 32
Summary
ERCOT, the Control Area Authority, has the responsibility of meeting the NERC Policy 1 Control Performance Standards.
ERCOT shall promptly take appropriate action to relieve any abnormal conditions that jeopardize reliable Interconnection operation.

## Slide 33
References
1 ERCOT Operating Guides
2 NERC Policy 1
3 Final Report of August 14, 2003 Blackout in the U.S. and Canada – May 2004.
4 SERC Operator Training Conference 2004, Generator Trip points.

## Slide 34: ERCOT Frequency Control
True/False
1. 80% of ERCOT’s Responsive Reserve Services may be provided as LAAR.

## Slide 35: ERCOT Frequency Control
2. In ERCOT, LAAR must be capable of interruption within how many cycles of the time that frequency decays to a value low enough to initiate action of the under-frequency relay(s)?
a. 20
b. 40
c. 60
d. 10

## Slide 36: ERCOT Frequency Control
3. In ERCOT, the LAAR initiation setting of the relay shall not be any lower than what Frequency
a. 59.7
b. 59.8
c. 59.81
d. 59.71

## Slide 37: ERCOT Frequency Control
4. ERCOT procures _____mw’s of Responsive Reserve Services for each Operating Hour.
a. 1150
b. 2300
c. 1300
d. 2600

## Slide 38: ERCOT Frequency Control
5. No less than 1150mw’s of ERCOT’s Responsive Reserve Services must be supplied by synchronized generation resources such as …
a. Generators, hydro units, and wind units
b. Generators, hydro units, and solar
c. Generators, hydro units, and DC ties
d. all of the above

## Slide 39: ERCOT Frequency Control
6. Responsive Reserve Services are operating reserves ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency
True/False

## Slide 40: ERCOT Frequency Control
7. ________________ are deployed every two seconds to regulation providers to balance Resources to Demand.
a. Responsive Reserve Services
b. Balancing Energy Services
c. Regulation Services
d. Non-Spin Reserve Services

## Slide 41: ERCOT Frequency Control
8. During Automatic Firm Load shedding; at what frequency does ERCOT shed the first 5%?
a. 58.9 Hz
b. 58.5 Hz
c. 59.91 Hz
d. 59.3 Hz

## Slide 42: ERCOT Frequency Control
9. If ERCOT’s Frequency dips to 58.5, a total Automatic Load Shed of ___% will occur.
a. 25
b. 20
c. 15
d. 10

## Slide 43: ERCOT Frequency Control
10. If ERCOT’s CPS1 score is above 90.0, it will pass CPS1
True/False

## Slide 44
Questions
?
?