## Slide 1
Black Start Plan
Ricson Chai / Frank Owens
2005 Annual Operations Seminar

## Slide 2
Introduction
What is this plan all about?
What are the Black Start Services?
What are the Black Start units?
How do we select these Black Start units?
How do we use them in the restoration process?
What shall I do during the restoration process?
And what are my responsibilities?

## Slide 3
Objectives
At the completion of this course you will:
Recognize the criteria used to select and qualify Black Start units.
Identify your roles as a market participant during the restoration process.
  Principles
  Strategies
  Priorities
  Responsibilities
Power System Concepts.

## Slide 4
Black Start Services
Black Start services are needed in the event of partial or complete collapse of electric system.
These services are provided by a set of contracted Black Start capable generation units.
These resources are re-evaluated annually.

## Slide 5
Black Start Units
These Black Start capable units are able to self-start without support from outside power.
Within close proximity of another power pools such as SPP, CFE, and WECC which are capable of starting from such power pool via a firm standby power supply contract can be qualified as a Black Start service.

## Slide 6
Black Start Unit Selection
Every year, black-start capable Resources entities submit their proposals to provide Black Start services for next year.
ERCOT uses the following selection criteria to select a set of units with minimum cost:
  Simulated restoration of 90% of ERCOT peak load within 48 hours.

## Slide 7
Black Start Unit Selection
ERCOT uses the following selection criteria to select a set of units with minimum cost: (Cont…)
  Expected restoration off-site power to nuclear units within 8 hours.
  Proximity of Black Start units to major load centers.
For those selected units, they will be under a series of tests to qualify their capabilities.

## Slide 8
Black Start Unit Selection
The selection criteria can be classified into two sets:
  Group selection criteria:
    Price ($/hour)
    Amount of MW pickup (55,000 MW)
    Restoration time (48 hours)
  Specific unit selection criteria:
    Black Start MW, next-start MW capacity, start-up time
    Proximity to nuclear plant
    Proximity to load centers

## Slide 9
Black Start Unit Selection
A Microsoft Access program was written to determine the best selection with fulfilling all the selection criteria in an automated fashion.
The program simulates the total unit start-up time, ramp-up time, crew travel time, and next-start ramp-up time to meet the selection criteria. Each unit will be continuously starting up other units without waiting for the other units.

## Slide 10
Black Start Unit Selection

## Slide 11
Black Start Unit Selection
 | Preferred Set
Plant # 1 | DECKER
Plant # 2 | ATKINS
Plant # 3 | MCSES
Plant # 4 | SPNCER
Plant # 5 | STEAM
Plant # 6 | BUCHAN
Plant # 7 | WFCOGEN
Plant # 8 | FLCNS
Plant # 9 | AMISTAD
Plant # 10 | FALCON
Plant # 11 | RAYBURN
Plant # 12 | SRB
Plant # 13 | THW
Plant # 14 | WAP
Plant # 15 | SCSES
MW Pickup | 55534
Restoration Time | 46.9
Cost | $6,191,830.80
This group selection has met the first criteria but it has not met the second and third criteria, they are :
  Simulated restoration of 55000 MW within 48 hours.
  Expected restoration off-site power to nuclear units within 8 hours.
  Proximity of Black Start units to major load centers.

## Slide 12
Black Start Unit Selection

## Slide 13
Two Black Start plants closest to the Comanche Peak are Decordova and Lake Creek.
Plant | Black Start MW | Next-Start MW | Hot Start-up Time | Cold Start-up Time
Decordova | 70 | 818 | 0.5 | 0.5
Lake Creek | 230 | 87 | 2 | 13
Black Start Unit Selection

## Slide 14
 | Initial Selection | Final Selection
Plant # 1 | DECKER | DECKER
Plant # 2 | ATKINS | ATKINS
Plant # 3 | MCSES | MCSES
Plant # 4 | SPNCER | SPNCER
Plant # 5 | STEAM | STEAM
Plant # 6 | BUCHAN | BUCHAN
Plant # 7 | WFCOGEN | WFCOGEN
Plant # 8 | FLCNS | FLCNS
Plant # 9 | AMISTAD | AMISTAD
Plant # 10 | FALCON | FALCON
Plant # 11 | RAYBURN | RAYBURN
Plant # 12 | SRB | SRB
Plant # 13 | THW | THW
Plant # 14 | WAP | WAP
Plant # 15 | SCSES | SCSES
Plant # 16 |  | DCSES
MW Pickup | 55534 | 55174
Restoration Time | 46.9 | 43.9
Cost | $6,191,830.80 | $6,936,430.80
Black Start Unit Selection

## Slide 15
2005 Black Start Selection

## Slide 16
Test Criteria
  Basic Start-up Test
  Line Energizing Test
  Load Carrying Test
  Start-up the largest motor at the next-start
  plant or simulate the scenario. (2006)
2005 Black Start Selection

## Slide 17
2005 Black Start Plan
In the event of a major system disturbance it is necessary to have procedures in place to cope with events and restore the system to normal state as quickly as possible.
ERCOT Black Start Plan incorporates restoration effort in case of partial or complete collapse of electric system.

## Slide 18
2005 Black Start Plan
What is in the Black Start Plan?
  Black Start map and transmission corridors
  Principles
  Strategies
  Priorities
  Responsibilities
    ERCOT
    TOs
    QSEs
    Resources

## Slide 19
Black Start Plan - Principles
Contracted Black Start Units
Local TO Plans
  Primary/secondary transmission corridors
  Designated synchronization points, primary and alternatives
Mutual assistance and cooperation
Restore the power system

## Slide 20
S
P
S
P
S
P
S
S
P
8040
Texas A&M
8030
8050
Greens Prairie
69001
8020
8030
8040
8050
8070
Atkins
Houston Island
Steephollow
Texas A&M Switch
South Switch
Dansby
Gibbons Creek
Stryker Creek Island
Black Start Plan - Principles
Example of Transmission Corridor

## Slide 21
Black Start Plan - Principles
Each contracted Black Start Plant and TO will have an internal Black Start Plan.
Plans identify Black Start units, primary and secondary Next-Start units, stabilizing loads, primary and secondary transmission corridors and synch points between islands.
The power system, not customers, is the principle focus during the restoration effort.

## Slide 22
Black Start Plan - Strategies
It is ERCOT’s opinion that all necessary information shared with affiliates for the restoration process is an allowed corporate support service under the provisions of PUCT rule 25.272.
In the event of total ERCOT blackout, the market is suspended.
39 contracted Black Start resources.
16 Black Start sites/islands.

## Slide 23
Black Start Plan - Strategies
The initial 16 islands will be built and maintained solely under the direction of the TOs as outlined in the TO Black Start Plans.
The TOs will be responsible for maintaining the appropriate voltage levels and reactive controls.
The TOs should periodically update ERCOT on the status of the islands during the restoration process.

## Slide 24
Black Start Plan - Strategies
These updates should coincide with the following events:
  A Black Start unit is brought on line.
  Any additional unit that is brought on line.
  A designated synchronization point between islands is reached.
  The TO needs to energize a piece of equipment that belongs to another TO.
  Any time a collapse or regression occurs in the restoration process.

## Slide 25
Black Start Plan - Priorities
Determine system conditions:
  Restore and maintain communications.
  Reliable communication will be the key to a safe and timely restoration.
If the primary communication is down, the backup system will be used.
Transmission corridors prepared to support restoration.
Secure and stabilize generating plants.

## Slide 26
Black Start Plan - Priorities
Communication paths:
ERCOT
TO
TO
PGC
TO
PGC
…
…

## Slide 27
Black Start Plan - Priorities
Contracted Black Start units will immediately bring their units on line.
Designated TOs will begin building islands to reach designated synch points.
Critical load priority:
  Nuclear generating facilities.
  Other generating units.
  ERCOT.
  Military and law enforcement facilities.
  Public health and communication facilities.

## Slide 28
Responsibilities - ERCOT
Maintain surveillance of ERCOT system status.
Central information collection and dissemination point.
Coordinate reconnection of transmission.
Direct the connection of separated islands.
Direct assistance for QSEs, TOs, PGCs, and market Particpants.

## Slide 29
Responsibilities - TO
Provide necessary personnel to assure capability of Black Start Plan restoration.
Coordinate communications for local Black Start units.
Coordinate switching to Next Start units and local load.
Act as a regional ERCOT representative in coordinating inter-connections of units.
Follow the direction of ERCOT for reconnection of islands.

## Slide 30
Responsibilities - QSE
Determine fuel options and capability of both Black Start units and Next Start units.
Supply ERCOT and/or local TO with information on the status of generation facilities that they represent.
Follow direction of TO or ERCOT in picking up load and starting Next Start units.
Provide assistance as directed by ERCOT or the local TO.

## Slide 31
Responsibilities - PGC
Black Start sites must first secure and stabilize on site generation that has tripped.
Communicate condition of Black Start/Next Start units to local QSE.
Communicate condition of fuel, water, and station service.
Implement Black Start Plan at the direction of TO/ERCOT.

## Slide 32
Concepts - Black Start Units
Timing is critical.
The coordination problem of re-energizing the grid is complicated.
Hydro, Combustion Turbines and Thermal Plants are likely Black Start units.
Generators have min. and max. load limits and max. ramp rates (MW/minute).
The balance of load and generation is very difficult when both are changing rapidly.

## Slide 33
Concepts - Generators
Plant operators will be controlling system frequency during initial stages of restoration.
AVRs should be placed in service as soon as practical to improve machine stability.
AGCs should be placed in automatic position to ensure instantaneous governor response to changes in load.

## Slide 34
Concepts - Transmission System
The transmission system itself presents a dynamic reactive load.
Transmission lines are highly capacitive when not loaded and voltages can easily become excessive.
R L
C
G
Load

## Slide 35
Concepts - Transmission System
Generators and reactors are used to hold voltages down.
Unfortunately, generators are less stable when they are absorbing reactive power.

## Slide 36
Concepts – Cold Load Pick-up
Initial load magnitude will be greater after energization.
Initial inrush currents can be ten or more times than the normal load current magnitude.
Motor model:
Ea
R
L

## Slide 37
Concepts – Energizing Lines
Carry at least 50% reserve with only a single generating unit on-line.
Keep at least 20% reserve once a second generating unit comes on-line.
Avoid closing a weak source into a fault possibly resulting in the loss of a unit.
Voltage regulators could be placed at lower than nominal set points prior to energizing lines to avoid over voltage due to line charging capacitance.

## Slide 38
Concepts – Synchronizing Point
When synchronizing two islands you must ensure the voltages are matched.
Synchronizing variables:
  Voltage magnitude difference.
  Voltage phase angle.
  Frequency difference.
Synch-check relay determines if the voltage, frequency and phase are matched.

## Slide 39
Concepts – Synchronizing Point
Synchroscopes are used to match the frequency and voltage phase angle.

## Slide 40
Summary
16 Black Start Resources.
ERCOT and TO Black Start Plans.
  Principles
  Strategies
  Priorities
  Responsibilities
Review system and equipment concepts.

## Slide 41
References
ERCOT Protocols
ERCOT Operating Guides
TO Local Black Start Plans
NERC Operating Guides.

## Slide 42
Questions
?
?

## Slide 43
Test Questions
Transmission lines are highly ____ when not loaded and voltages can easily become excessive.
capacitive
inductive
reactive
both a and b

## Slide 44
Test Questions
Initial inrush currents can be ___ or more times than the normal load current magnitude.
ten
five
twenty
fifty

## Slide 45
Test Questions
AVRs should be placed in service as soon as practical to improve machine stability.
True or False

## Slide 46
Test Questions
AGCs should be placed in the off position to ensure instantaneous governor response to changes in load.
True or False

## Slide 47
Test Questions
Synchroscopes are used to match the ___ and voltage phase angle when synchronizing systems.
frequency
amps
ohms
none of the above

## Slide 48
Test Questions
Every ___, black-start capable resources entities submit their proposals to provide Black Start services.
day
year
month
two years

## Slide 49
Test Questions
ERCOT uses the following selection criteria to select a set of units with minimum cost.
Simulated restoration of 90% of ERCOT peak load within 48 hours.
Expected restoration off-site power to nuclear units within 8 hours.
Proximity of Black Start units to major load centers.
All of the above.

## Slide 50
Test Questions
___ incorporates restoration effort in case of partial or complete collapse of electric system.
ERCOT Black Start Plan
ERCOT Protocols
ERCOT Operating Guides
ERCOT Market Guides

## Slide 51
Test Questions
Which of the following is not one of ERCOT’s responsibilities in a Black Start situation?
Maintain surveillance of ERCOT system status.
Act as a central information collection and dissemination point.
Coordinate and issue switching orders for the cooperatives and municipalities.
Direct the connection of separated islands.

## Slide 52
Test Questions
Which of the following is not a responsibility of a QSE in a Black Start situation?
Supply ERCOT and/or local TO with information on the status of generation represented.
Follow direction of TO or ERCOT in picking up load and starting Next Start units.
Provide assistance as directed by ERCOT or the local TO.
None of the above.

## Slide 53
Test Questions
Which of the following is not a Black Start selection criterion?
Simulated restoration of 90% of ERCOT peak load within 48 hours.
Minimized the total cost/payment.
Expected restoration off-site power to nuclear units within 8 hours.
Proximity of Black Start units to major load centers.

## Slide 54
Test Questions
Which of the following is a new requirement in the Black Start qualification tests?
Start up the next-start unit’s largest required motor.
Line energizing test.
Load carrying test.
None of the above.