## Slide 1: ERCOT Outage Coordination and Approval

## Slide 2: Robert Matlock/Hubert Smith
Outage Coordinator
ERCOT

## Slide 3: Goal
To have a better understanding of the ERCOT outage approval process.

## Slide 4: Objectives
Identify study periods and approval/rejection time frames for transmission and resource outage requests.
Identify the responsibilities for entering forced outages.
Identify the challenges involved with coordinating outages.

## Slide 5: Protocol requirements for Outage Scheduling
8.1.3.1 Transmission Facilities
TSPs must provide ERCOT a written Planned Outage or Maintenance Outage program in an ERCOT provided format for the next twelve (12) months updated monthly for a rolling twelve (12) month period. Planned Outage or Maintenance Outage scheduling data for Transmission Facilities shall be kept current. Updates must identify all changes to any previously proposed Planned Outages or Maintenance Outage and any additional Planned Outages or Maintenance Outage anticipated over the next twelve (12) months. ERCOT will coordinate in-depth reviews of the twelve (12) month programs with the TSPs at least two (2) times a year.
Transmission outages are posted on the ERCOT web site at:
http://www.ercot.com/Participants/PublicMarketInfo/PublicMarketInformation.htm

## Slide 6: Protocol requirements for Outage Scheduling cont.
8.1.3.2 Resources
Resource Entities must provide ERCOT a written Planned Outage and Maintenance Outage program for the next twelve (12) months, in an ERCOT provided format updated for a rolling twelve (12) month period. Planned Outage and Maintenance Outage scheduling data for Resource Facilities shall be kept current. Updates shall identify any changes to previously proposed Planned Outages or Maintenance Outages and any additional Planned Outages or Maintenance Outage anticipated over the next twelve (12) months.

## Slide 7
ERCOT Outage Study Periods for Transmission Planned Outages
Requested greater than 45 Days before the planned start date:
    Approved or rejected no later than 30 days prior to the planned start date
Requested 9 to 45 days before the planned start date:
    Approved or rejected no later than 00:00 4 days prior to the planned start date
Requested 4 to 8 days before the planned start date:
    Approved or rejected no later than 00:00 2 days prior to the planned start date
Requested 3 days before the planned start date:
    Approved or rejected no later than 00:00 1 day prior to the planned start date (Protocol 8.3.3 )

## Slide 8
Transmission Outage Approval Timelines

## Slide 9: ERCOT Outage Study Periods for Resource Planned Outages
Requested > 8 days before the planned start date:
    Accepted upon request
Requested 3 to 8 days before the planned start date:
    Accepted or rejected no later than 00:00 2 days prior to the planned start date
Requested 1 to 2 days before the planned start date:
    Accepted or rejected within 8 Business hours of receipt by ERCOT
    (Protocol 8.4.4)

## Slide 10: Reliability Resource Units
Reliability Must Run Units (RMR)
Synchronous Condenser Unit
Black Start Resource

## Slide 11: ERCOT Outage Study Periods for Reliability Resource Units Planned outages
Requested > 45 days before the planned start date:
    Approved or rejected no later than 30 days prior to the planned start date
Requested 30 to 45 days before the planned start date:
    Approved or rejected no later than 15 days prior to the planned start date
    (Protocol 8.5)
Notes: Protocol 8.5 defines Reliability Resources as:
Reliability Must Run units (RMR) - A Generation Resource unit operated under the terms of an Agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria where Market Solutions do not exist.
Synchronous Condensers - A unit operated under the terms of an annual Agreement with ERCOT that is only capable of supplying Volt Amperes Reactive (VAR) that would not otherwise be operated except that it is necessary to provide voltage support under first contingency criteria where Market Solutions do not exist.
Black Start units - A contracted Ancillary Service acquired by ERCOT for the benefit of all Loads, provided by Resource capable of starting without support of the ERCOT Transmission Grid.
Per Protocol 8.5.1 Reliability Resource Outage requests submitted greater than 45 days click before the planned start date of the outage will be approved or rejected click 30 days prior to the start of the outage
click
Outage requests submitted 30 to 45 days before the planned start will be approved or rejected click 15 days prior to the start of the outage
Outage Requests on Reliability Resource units submitted < 30 days before the planned start date must be Maintenance outages.
click to next slide

## Slide 12: Reliability Resource Units outages requested less then 30 days before the planned start date
    Outage requests on Reliability Resource Units requested less than 30 days before the planned start date must be entered as a Maintenance Outage.
Notes: Protocol 8.5 defines Reliability Resources as:
Reliability Must Run units (RMR) - A Generation Resource unit operated under the terms of an Agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria where Market Solutions do not exist.
Synchronous Condensers - A unit operated under the terms of an annual Agreement with ERCOT that is only capable of supplying Volt Amperes Reactive (VAR) that would not otherwise be operated except that it is necessary to provide voltage support under first contingency criteria where Market Solutions do not exist.
Black Start units - A contracted Ancillary Service acquired by ERCOT for the benefit of all Loads, provided by Resource capable of starting without support of the ERCOT Transmission Grid.
Per Protocol 8.5.1 Reliability Resource Outage requests submitted greater than 45 days click before the planned start date of the outage will be approved or rejected click 30 days prior to the start of the outage
click
Outage requests submitted 30 to 45 days before the planned start will be approved or rejected click 15 days prior to the start of the outage
Outage Requests on Reliability Resource units submitted < 30 days before the planned start date must be Maintenance outages.
click to next slide

## Slide 13
Maintenance Outages requested between 9 and 30 days prior to the planned start date (Maintenance Level III):
    Approved or rejected no later than 4 days prior to the planned start date
Maintenance Outages requested between 3 and 8 days prior to the planned start date (Maintenance Level II):
    Approved or rejected no later than 00:00
    2 days prior to the planned start date
    (Protocol 8.51)
ERCOT Outage Study Periods for Reliability Resource Units Maintenance Outages
Notes: click
Reliability Resource Maintenance Outage requests submitted between 9 and 30 days before the planned start date will be approved or rejected click no later than 4 days prior to the start of the outage.
click
Reliability Resource Maintenance Outage requests submitted between 3 and 8 days before the planned start date will be approved or rejected click no later than 00:00 2 days prior to the start of the outage.
click to next slide

## Slide 14: Resource Outage Acceptance Timeline

## Slide 15: ERCOT Outage Study Periods for Transmission and Resource Maintenance Outages
Maintenance Level 1
Maintenance Level 2
Maintenance Level 3
All Maintenance Level outages are Accepted by ERCOT but will be coordinated by ERCOT within the time frames of the Maintenance outage type.

## Slide 16: Maintenance Outages
Removing Transmission Facility or Resource Facility equipment from service to perform work on specific Facility components that could be postponed briefly. Such work is required to prevent a potential Forced Outage and cannot be postponed until the next Planned Outage. Such Maintenance Outages are classified as follows:
(1) Level 1 Maintenance Outage – Equipment that must be removed from service within twenty-four (24) hours to prevent a potential Forced Outage;
(2) Level II Maintenance Outage – Equipment that must be removed from service within seven (7) days to prevent a potential Forced Outage; and
Level III Maintenance Outage – Equipment that must be removed from service within thirty (30) days to prevent a potential Forced Outage.
(Protocol 2.1)

## Slide 17: Forced Outages!
Forced and Maintenance outages shall be
communicated to ERCOT immediately by
voice communication and subsequently
entered into the Outage Scheduler.
(Protocol 8.2.2)

## Slide 18
Challenges with coordinating outages
To keep the ERCOT system secure.
Work with the transmission operators and resource entities/QSE’s to allow outages on there equipment while adhering to the ERCOT Protocols, procedures and guides.
Keep the ERCOT real time operation and engineering support informed of upcoming problematic outages.

## Slide 19: The Approval Process

## Slide 21: Protocol 8.1.1
ERCOT will coordinate and use reasonable efforts, consistent with Good Utility Practice, to accept or approve all Outage schedules for maintenance, repair, and construction of both Transmission and Resources Facilities within the ERCOT System.

## Slide 22: Good utility practice
Any of the practices, methods, and acts engaged in or approved by a significant portion of the electric utility industry during the relevant time period, or any of the practices, methods, and acts that, in the exercise of reasonable judgment in light of the facts known at the time the decision was made, could have been expected to accomplish the desired result at a reasonable cost consistent with good business practices, reliability, safety, and expedition. Good utility practice is not intended to be limited to the optimum practice, method, or act, to the exclusion of all others, but rather is intended to include acceptable practices, methods, and acts generally accepted in the region.
  (From PUCT document: “SUBSTANTIVE RULES”; “APPLICABLE TO ELECTRIC SERVICE PROVIDERS” - CHAPTER 25; Subchapter A. “GENERAL PROVISIONS” number 56)

## Slide 23
Considerations
Peak demand conditions
Current generation pattern
Expected generation pattern
Planned Outages
Maintenance Outages
Forced Outages
Pre and Post contingent violations (thermal and voltage)
Study Process

## Slide 24: Study Process Cont.
  Determine the hour/hours you are going to study considering:
    Load
    Start and End times of the days outages
    Weather

## Slide 25
  Using AREVA - EMMS software, setup an STNET (Study Network Analysis) case for one the times you are studying.
    Open a base case
    Set the Date/time
    Set the load
    Make generation adjustments
    Import dynamic line ratings
    Run power flow and contingency analysis
    Clear pre and post contingent thermal and voltage violations
Study Process Cont.

## Slide 26: Study Process Cont.
Studying Outages
  Import outages
  Run Power flow
  Adjust generation
  Run Power flow and contingency analysis
  Check for base case and post contingent voltage and thermal violations
  Attempt to clear pre and post contingent violations
  Approve/reject outages

## Slide 27: Study Process Cont.
If contingencies can’t be cleared by adjusting generation within Units normal operating range:
  Determine the outage/outages may be causing the violation.
  Work with the TO’s to determine if the network model is correct. I.E. line limits, transformer limits etc.
  Work with the TO’s to see if there may be a switching action to clear the violation.
  If a solution can’t be found the outage may be rejected.

## Slide 28: Study Process Cont.
Adjusting Generation outside the normal operating range to clear violations due to an outage:
  Outages of this nature may require more study and should be submitted in the 9 to 45 day or the > 45 day study period.

## Slide 29: Study Process Cont.
  Repeat the process for each hour you determined a study is needed for the day you are looking at.

## Slide 30: Daily Outage Report for two days from today is published and outages are printed
Post Study Process

## Slide 31
Morning meeting with ERCOT operators on today's outages
Daily Outage Notes for two days from today are given to the ERCOT operations engineer on call and the ERCOT Trans/Security Desk, Day Ahead Desk and Shift Supervisors Desk each afternoon after 15:00
Afternoon meeting with ERCOT operators on the next days outages
Post Study Process

## Slide 32
Questions ???

## Slide 33
OUTAGES
REVIEW QUESTIONS
1. ERCOT Protocols require submission of a written Planned Outage and Maintenance Outage schedule for:
a. All Transmission facility outages
b. All Resource facility outages
c. All Forced outages
d. Both a & b

## Slide 34
OUTAGES
REVIEW QUESTIONS
2. Outages required to be posted on the ERCOT web site (www.ercot.com) are:
a. All outages
b. All Transmission outages
c. All Generation outages
d. Only significant outages

## Slide 35
OUTAGES
REVIEW QUESTIONS
3. Planned resource outages that are submitted greater than 8 days before the outage starts will be
a. accepted
b. approved immediately
c. approved or rejected at least 3 days prior to the start
d. approved or rejected at least 5 days prior to the start

## Slide 36
OUTAGES
REVIEW QUESTIONS
4. Planned Outage and Maintenance Outage scheduling data is updated:
a. For Six months at a time
b. For a rolling 12 month period
c. Annually
d. Monthly

## Slide 37
OUTAGES
REVIEW QUESTIONS
5. Planned resource outages that are submitted 3 to 8 days before the outage starts will be
a. rejected
b. approved immediately
c. approved or rejected at least 2 days prior to the start
d. approved or rejected at least 1 days prior to the start

## Slide 38
OUTAGES
REVIEW QUESTIONS
6. Planned transmission outages that are submitted 4 to 8 days before the outage starts will be approved or rejected at least:
a. 1 day prior to the start
b. 2 days prior to the start
c. 4 days prior to the start
d. 30 days prior to the start

## Slide 39
OUTAGES
REVIEW QUESTIONS
Planned transmission outages that are submitted greater than 45 days before the outage starts will be approved or rejected at least:
a. 1 day prior to the start
b. 2 days prior to the start
c. 4 days prior to the start
d. 30 days prior to the start

## Slide 40
OUTAGES
REVIEW QUESTIONS
8. Planned transmission outages that are submitted 3 days before the outage starts will be approved or rejected at least:
a. 1 day prior to the start
b. 2 days prior to the start
c. 4 days prior to the start
d. 30 days prior to the start

## Slide 41
OUTAGES
REVIEW QUESTIONS
9. Planned resource outages that are submitted 1 to 2 days before the outage starts will be
a. rejected
b. approved immediately
c. approved or rejected within 1 day of receipt
d. approved or rejected within 8 business hours of receipt

## Slide 42
OUTAGES
REVIEW QUESTIONS
10. Planned transmission outages that are submitted 9 to 45 days before the outage starts will be approved or rejected at least:
a. 1 day prior to the start
b. 2 days prior to the start
c. 4 days prior to the start
d. 30 days prior to the start

## Slide 43
OUTAGES
REVIEW QUESTIONS
11. Planned outages of RMR units that are submitted greater than 45 days before the outage starts will be
a. rejected
b. approved immediately
c. approved or rejected at least 15 days prior to the start
d. approved or rejected at least 30 days prior to the start

## Slide 44
OUTAGES
REVIEW QUESTIONS
12. Planned outages of Blackstart units that are submitted less than 45 days but greater than 30 days before the outage starts will be
a. accepted
b. approved immediately
c. approved or rejected at least 8 days prior to the start
d. approved or rejected at least 15 days prior to the start

## Slide 45
OUTAGES
REVIEW QUESTIONS
13. Forced and Maintenance Level 1 outages shall be communicated to ERCOT by voice communication
a. Immediately
b. As soon as practicable
c. Within one hour of start time
d. Within one working day of start time

## Slide 46
OUTAGES
REVIEW QUESTIONS
14. Forced and Maintenance Level 1 outages are to be entered in the Outage Scheduler
a. By the ERCOT Transmission and Security Desk Operator
b. By the QSE or TSP responsible for the facility
c. Immediately
d. Within 24 hours of the start of the outage

## Slide 47
OUTAGES
REVIEW QUESTIONS
15. The primary challenge associated with coordinating outages is
a. Keeping the ERCOT system within single-contingency criteria
b. Keeping track of all of the outages
c. Making sure outages are always approved
d. Ensuring all outages are approved as requested