## Slide 1
ERCOT Guides
Section 4
Emergency
Operations

## Slide 2: Introduction
Emergency operation is intended to address operating conditions under which the reliability of the ERCOT System is inadequate and there is no Market Solution readily apparent. During a declared system emergency, ERCOT can instruct TDSPs and QSEs to take specific operating actions that would otherwise be discretionary.

## Slide 3: Objectives
Identify the four ERCOT emergency communications
Identify the purpose of each ERCOT emergency communication
Identify the purpose of each EECP step
Identify the basis for ERCOT transmission system reliability assessments
Identify the basis for terminating EECP

## Slide 4: Definitions
QSE - A Market Participant that is qualified by ERCOT in accordance with Section 16, Registration and Qualification of Market Participants, to submit Balanced Schedules and Ancillary Services bids and settle payments with ERCOT.
REP - A person that sells electric energy to retail Customers in this state. As provided in PURA §31.002(17), a Retail Electric Provider may not own or operate generation assets. As provided in PURA §39.353(b), a Retail Electric Provider is not an Aggregator.
MIS - An electronic communications interface established and maintained by ERCOT that provides a communications link to Market Participants, including secure access by and communications to individual Market Participants regarding information linked to each individual Market Participant.
RMR - A Generation Resource unit operated under the terms of an Agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria where Market Solutions do not exist.
OOM - Outside the bidding process to resolve a reliability or security event when no Market Solution exists.
TDSP - An Entity that owns or operates for compensation in this state equipment or Facilities to transmit and/or distribute electricity, and whose rates for Transmission Service, distribution service, or both is set by a Governmental Authority.

## Slide 5: Annual System Operator Training Requirements
NERC Board Approved Blackout Recommendations, February 10, 2004
Recommendation 6. Improve Operator and Reliability Coordinator Training
All reliability coordinators, control areas and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system.

## Slide 6: Situational Awareness
Weather
  Freezing temperatures
  Excessive heat
  Severe Storms
System Loading
  Congestion
  Forced Outages
  Equipment Ratings
Sabotage

## Slide 7: Minimum Standards for Reliability
Minimum operating reserve levels
Acceptable frequency control
Maintain voltage within limits
Maximum transmission equipment loading levels
Unacceptable risk of widespread cascading outages

## Slide 8: Single Contingency Criteria
Generation
    The Forced Outage of two generating units in the ERCOT System within a short period of time .
Transmission
    The Forced Outage of any single transmission element (such as a circuit or transformer).
    The Forced Outage of a double-circuit transmission line (DCKT) will be considered a credible single contingency
Notes: ERCOT Operators are responsible for operating the ERCOT Transmission systems within first contingency transfer limits so that there is no overload of any significant transmission element whose loss could jeopardize the reliability of the ERCOT System. Whenever the ERCOT System is not engaged in emergency operation, it will be operated in such a manner that the occurrence of a single contingency will not cause any of the following:
a. Uncontrolled breakup of the transmission system,
b. Loading of Transmission Facilities above defined emergency ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures,
c. Transmission voltage levels outside system design limits which can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs, or
d. Customer outages, except for high set interruptible and radially served loads.
“Single contingency” criteria are specified as follows:
A credible single contingency is defined as the Forced Outage of two generating units in the ERCOT System within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer).
The Forced Outage of a double-circuit transmission line (DCKT) will be considered a credible single contingency for any of the following operating conditions characterized by high DCKT Outage probability or consequence:
High Outage Probability
Severe weather conditions are forecasted by ERCOT in the vicinity of the DCKT.
Weather conditions indicate a high risk of insulator flashover on the DCKT.
Individual circuits that are part of the DCKT have experienced repeated Forced Outages within the preceding 48 hours possibly indicating unresolved problems.
A high risk of DCKT Outage exists due to fire in progress near the DCKT right-of-way.
High Outage Consequence
Another transmission Facility, which significantly increases the impact of an Outage to the DCKT, is out of service.
Studies indicate Outage of the DCKT would result in cascading outages or voltage collapse.
Studies indicate Outage of the DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures in time to prevent equipment damage or failure.

## Slide 9: Market Solution
If practicable, the market must be allowed to work to mitigate or eliminate any possible Emergency Condition. ERCOT has the responsibility to issue the appropriate communications to facilitate a Market Solution to the problem.
Notes: Before deciding which emergency communication to issue, ERCOT must consider the possible severity of the operating situation and the time and resources available for the market to respond before an Emergency Condition occurs. If practicable, the market must be allowed to work to mitigate or eliminate any possible Emergency Condition. ERCOT has the responsibility to issue the appropriate communications to facilitate a Market Solution to the problem.

## Slide 10: Communication
Before deciding which emergency communication to issue, ERCOT must consider the possible severity of the operating situation and the time and resources available for the market to respond before an Emergency Condition occurs.
During a declared system emergency, ERCOT can instruct TDSPs and QSEs to take specific operating actions that would otherwise be discretionary.

## Slide 11: Communication
ERCOT may issue communications in the form of Notices, Advisories, Alerts and Emergency Notices. These communications may relate to weather, transmission, distribution, and/or generation information and shall specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. These communications will be issued by ERCOT to inform all , Transmission Operators (TOs) and QSEs of the current operating situation.
Notes: Emergency operation is intended to address operating conditions under which the reliability of the ERCOT System is inadequate and there is no Market Solution readily apparent. During a declared system emergency, ERCOT can instruct TDSPs and QSEs to take specific operating actions that would otherwise be discretionary. Upon receiving Valid Dispatch Instruction from ERCOT, and in compliance with the Operating Guides, the QSEs shall direct relevant Resources or groups of Resources to respond to the instruction ERCOT shall coordinate with QSEs and TDSPs to assure that necessary actions are taken to maintain service reliability under any circumstances.
It is essential that good, timely, and accurate communication routinely occur between ERCOT, TDSPs, and QSEs. QSE and TDSP personnel will report unplanned equipment status changes as outlined in Section 4 of this ERCOT Operating Guide. ERCOT System Operators may ask for status updates as required in order to gather information to make decisions on system conditions to determine what type of emergency communication may be appropriate.
ERCOT may issue communications in the form of Notices, Advisories, Alerts and Emergency Notices. These communications may relate to weather, transmission, distribution, and/or generation information and shall specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. These communications will be issued by ERCOT to inform all , Transmission Operators (TOs) and QSEs of the current operating situation. TOs will notify their represented TDSPs, and QSEs will in turn notify the appropriate Resources and REPs. QSEs and TDSPs should establish and maintain internal procedures for contingency preparedness or to expedite the resolution of the conditions communicated by ERCOT that threatens system reliability.
Before deciding which emergency communication to issue, ERCOT must consider the possible severity of the operating situation and the time and resources available for the market to respond before an Emergency Condition occurs. If practicable, the market must be allowed to work to mitigate or eliminate any possible Emergency Condition. ERCOT has the responsibility to issue the appropriate communications to facilitate a Market Solution to the problem.

## Slide 13: Operating Condition Notice
An Operating Condition Notice (OCN) will be issued by ERCOT to inform all QSEs of a possible future need for more Resources because of conditions that could affect reliability. OCNs are for communication only, and ERCOT exercises no extra authority with the issuance of this type of notice.
Notes: An Operating Condition Notice (OCN) will be issued by ERCOT to inform all QSEs of a possible future need for more Resources because of conditions that could affect reliability. OCNs are for communication only, and ERCOT exercises no extra authority with the issuance of this type of notice.
When time permits, ERCOT will issue an OCN prior to issuance of an Advisory, Alert, or Emergency Notice. However, issuance of an OCN does not require action on the part of any Market Participant, but rather simply serves as a reminder for QSEs and TDSPs that some attention to the changing condition may be warranted. OCNs serve to communicate to QSEs the need to take extra precautions to be prepared to serve the Load during times when contingencies are most likely to arise.
Weather-related OCNs include notices of anticipated freezing temperatures, hurricanes, wet weather, and ice storms as provided to ERCOT by TDSPs. An example of another type of OCN is notice of unplanned transmission outages. ERCOT will monitor actual and forecasted weather for ERCOT and adjacent NERC Regions. When adverse weather conditions are expected, ERCOT may confer with TDSPs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. QSEs and TDSPs are expected to establish and maintain internal procedures for monitoring actual and forecasted weather and for implementing appropriate measures when the potential for adverse weather or other conditions arise which could threaten ERCOT System reliability.

## Slide 15: Advisory
An Advisory will be issued by ERCOT when it recognizes that conditions are developing or have changed such that QSE or TDSP action is prudent in response to impending severe conditions
An Advisory may be issued in response to:
Concern at ERCOT about the availability of Resources to serve anticipated demand
Projected insecure conditions due to unacceptable loading conditions
Communication or control limitations
The Advisory communicates what constraints or insecure states are expected.

## Slide 16: Advisory Actions
An Advisory is for communication but, with the issuance of an Advisory, ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities specified in the normal Day-Ahead plan in accordance with scheduling procedures. ERCOT may also increase the Day-Ahead market to Two-Days-Ahead.
Notes: An Advisory will be issued by ERCOT when it recognizes that conditions are developing or have changed such QSE or TDSP action is prudent in response to impending severe conditions.
An Advisory may be issued in response to:
Concern at ERCOT about the availability of Resources to serve anticipated demand
Projected insecure conditions due to unacceptable loading conditions
Communication or control limitations
The Advisory communicates what constraints or insecure states are expected.
In the event of an Advisory, ERCOT will notify TOs and QSEs and post the information on the MIS.
QSEs will notify appropriate Resources and REPs.
TOs will notify their represented TDSPs as appropriate.
An Advisory is for communication, but with the issuance of an Advisory ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities specified in the normal Day-Ahead plan in accordance with scheduling procedures. ERCOT may also increase the Day-Ahead market to Two-Days-Ahead.
ERCOT will communicate with TDSPs as needed to confirm their understanding of the condition and to determine availability of equipment and Resources. For the purpose of verifying submitted information, ERCOT may also communicate with QSEs.

## Slide 18: Alert
An Alert may be issued by ERCOT when it recognizes that conditions have developed such that an insecure operating state exists or is imminent.
An Alert may also be issued by ERCOT when it recognizes that market Congestion Management techniques specified in these protocols will not be adequate to resolve transmission problems.
Notes: An Alert may be issued by ERCOT when it recognizes that conditions have developed such that an insecure operating state exists or is imminent.
With the issuance of an Alert, ERCOT may exercise its authority to ask for a quick bid response that precludes the QSEs having sufficient time to Self-Arrange additional Ancillary Services (Regulation Services, Responsive Reserve Services, and Non-Spinning Reserve Services). These additional Ancillary Services bids must be submitted by the market promptly in compliance with the Scheduling Protocol (within 15 minutes).
An Alert may also be issued by ERCOT when it recognizes that market Congestion Management techniques specified in these protocols will not be adequate to resolve transmission problems.
Alerts will be issued by ERCOT when Forced Outages or other abnormal operating conditions occur which require operations outside first contingency security limits. ERCOT will notify all TOs and QSEs and will post the Alert. TOs should notify their represented TDSPs. QSEs should notify appropriate resources and REPs. Identified corrective actions shall be implemented. To minimize the effects on the ERCOT System, all TDSPs will identify and prepare to implement actions, including restoring outaged lines as appropriate and preparation for Load shedding. ERCOT may instruct reconfiguration of ERCOT System elements by TDSPs necessary to improve the reliability of ERCOT as a whole. On notification of an Alert, each QSE and TDSP will prepare for an Emergency in case conditions worsen.

## Slide 19: Alert (cont.)
Alerts will be issued by ERCOT when Forced Outages or other abnormal operating conditions occur which require operations outside first contingency security limits.

## Slide 20: Alert Actions
With the issuance of an Alert, ERCOT may exercise its authority to ask for a quick bid response that precludes the QSEs having sufficient time to Self-Arrange additional Ancillary Services.
These additional Ancillary Services bids must be submitted by the market promptly in compliance with the Scheduling Protocol (within 15 minutes).

## Slide 21: Alert Actions (cont.)
To minimize the effects on the ERCOT System, all TDSPs will identify and prepare to implement actions, including restoring outaged lines as appropriate and preparation for Load shedding.
On notification of an Alert, each QSE and TDSP will prepare for an Emergency in case conditions worsen.
Notes: An Alert may be issued by ERCOT when it recognizes that conditions have developed such that an insecure operating state exists or is imminent.
With the issuance of an Alert, ERCOT may exercise its authority to ask for a quick bid response that precludes the QSEs having sufficient time to Self-Arrange additional Ancillary Services (Regulation Services, Responsive Reserve Services, and Non-Spinning Reserve Services). These additional Ancillary Services bids must be submitted by the market promptly in compliance with the Scheduling Protocol (within 15 minutes).
An Alert may also be issued by ERCOT when it recognizes that market Congestion Management techniques specified in these protocols will not be adequate to resolve transmission problems.
Alerts will be issued by ERCOT when Forced Outages or other abnormal operating conditions occur which require operations outside first contingency security limits. ERCOT will notify all TOs and QSEs and will post the Alert. TOs should notify their represented TDSPs. QSEs should notify appropriate resources and REPs. Identified corrective actions shall be implemented. To minimize the effects on the ERCOT System, all TDSPs will identify and prepare to implement actions, including restoring outaged lines as appropriate and preparation for Load shedding. ERCOT may instruct reconfiguration of ERCOT System elements by TDSPs necessary to improve the reliability of ERCOT as a whole. On notification of an Alert, each QSE and TDSP will prepare for an Emergency in case conditions worsen.

## Slide 23: Emergency Notification
ERCOT is considered to be in an insecure state whenever ERCOT Transmission Grid status is such that the most severe single-contingency even presents the threat of uncontrolled separation, cascading outages and/or large-scale service disruption to Load (other than Load being served from a single-feed transmission service) and/or overload of a critical transmission element, and no timely solution is obtainable from the Market.

## Slide 24: Emergency Notification (cont)
ERCOT will only issue an Emergency Notice when it recognizes that immediate action is required because:
ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market
ERCOT must avoid or relieve an overloaded transmission element
ERCOT is in an insecure state
ERCOT varies from Timing Requirements or omits one or more Scheduling Procedures

## Slide 25: Emergency Notification Actions
The actions ERCOT takes during a declared emergency will depend on the nature and severity of the situation. If the emergency is the result of a transmission problem that puts ERCOT in an insecure state, then ERCOT will act immediately to return ERCOT to a reliable condition, including instructing Resources to change output and instructing TDSPs to drop Load. TDSPs and Resources are required to implement the instructions and notify ERCOT when actions are complete.
Notes: ERCOT is considered to be in an insecure state whenever ERCOT Transmission Grid status is such that the most severe single-contingency even presents the threat of uncontrolled separation of cascading outages and/or large-scale service disruption to Load (other than Load being served from a single-feed transmission service) and/or overload of a critical transmission element, and no timely solution is obtainable from the market.
ERCOT will only issue an Emergency Notice when it recognizes that immediate action is required because:
ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market
ERCOT must avoid or relieve an overloaded transmission element
ERCOT is in an insecure state
ERCOT varies from Timing Requirements or omits one or more Scheduling Procedures
The actions ERCOT takes during a declared emergency will depend on the nature and severity of the situation. If the emergency is the result of a transmission problem that puts ERCOT in an insecure state, then ERCOT will act immediately to return ERCOT to a reliable condition, including instructing Resources to change output and instructing TDSPs to drop Load. TDSPs and Resources are required to implement the instructions and notify ERCOT when actions are complete.
If the emergency is the result of a short supply situation, then the Emergency Curtailment Plan procedures will be followed.

## Slide 26
NEW
ERCOT Oper. Bulletin #153
Purpose:
Complying with NERC requirements for recovering from a reportable DCS event
DCS Event:
MSSC – Most Severe Single Contingency
ERCOT – 1250MW (STP, CPK)
Multiple Contingencies
Reportable DCS Event:
80% of MSSC (1000MW)

## Slide 27
NERC Recovery Criteria:
Pre-disturbance Conditions
Frequency > 60 Hz (schedule)
Restore frequency to 60 Hz within 15 minutes
Frequency < 60 Hz (schedule)
Restore frequency to pre-disturbance value in 15 minutes
ERCOT Oper. Bulletin #153

## Slide 28
60
59.7
00:00
00:15
60
59.7
00:00
00:15
ERCOT Oper. Bulletin #153
Recovery Criteria Detail

## Slide 29
Procedure:
ERCOT Operator (Frequency Desk) will determine (immediate action) if the event is a Reportable DCS Event (1000MW)
Not Reportable – proceed with normal operations
Reportable – Emergency Notification Event (action required)
ERCOT Oper. Bulletin #153

## Slide 30
ERCOT CAA Actions
Prerequisites:
POTENTIAL Reportable DCS Event
Frequency above 59.7
Immediately deploy LAARs via hotline call to QSEs
Immediately deploy hydro units bid to supply responsive reserves via hotline call
ERCOT Oper. Bulletin #153

## Slide 31
ERCOT CAA Actions (cont.)
Transmission & Security Desk
Notify TOs that LAARs are being deployed
Restoration After Event:
Incrementally as conditions permit
Notify TOs that LAARs are being restored
ERCOT Oper. Bulletin #153

## Slide 32
Possible Penalties Imposed by NERC
Increase in contingency reserves equal to the amount of the violation for three months.
ERCOT Oper. Bulletin #153

## Slide 33: Emergency Electric Curtailment Plan
At times it may be necessary to reduce electrical demand because of a temporary shortfall in available electricity supply. The reduction in supply could be caused by emergency outages of generators, transmission equipment, or other critical facilities; by short-term unavailability of fuel or generation; or by requirements or orders of government agencies .
Notes: 4.5.1 General
At times it may be necessary to reduce electrical demand because of a temporary shortfall in available electricity supply. The reduction in supply could be caused by emergency outages of generators, transmission equipment, or other critical facilities; by short-term unavailability of fuel or generation; or by requirements or orders of government agencies. To provide an orderly, predetermined procedure for curtailing demand during such emergencies, ERCOT has established this Emergency Electric Curtailment Plan.
The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.
4.5.2 Operating Procedures
The ERCOT System Operators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions. ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a partial or complete system shutdown. These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service. TDSPs will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting load, notifying others and restoration of service.
ERCOT and each TDSP will endeavor to maintain transmission ties intact if at all possible. This will: (1) permit rendering the maximum assistance to an area experiencing a deficiency in generation, (2) minimize the possibility of cascading loss to other parts of the system, and (3) assist in restoring operation to normal.
ERCOT's operating procedures will meet the following goals while continuing to respect the confidentiality of market sensitive data. If all goals cannot be respected simultaneously then the priority order listed below shall be respected:
Maintain station service for nuclear generating facilities.
Securing startup power for power generating plants.
Operating generating plants isolated from ERCOT without communication.
Restoration of service to critical loads such as:
Military facilities
Facilities necessary to restore the electric utility system
Law enforcement organizations and facilities affecting public health
Communication facilities
Maximum utilization of ERCOT System Capability.
Utilization of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions.
Utilization of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT System.
Restoration of service to all customers following major system disturbances, giving priority to the larger group of customers.
4.5.3 Implementation
ERCOT shall be responsible for monitoring system conditions, initiating the EECP steps below, notifying all QSEs and TOs, and coordinating the implementation of the EECP Conditions while maintaining transmission security limits. QSEs and TOs will notify all the Market Participants they represent of each ERCOT declared EECP Step.
ERCOT has the authority to obtain Emergency Assistance energy over the DC tie(s) for use by ERCOT. ERCOT is also the coordinating authority for requests for emergency type power into or out of ERCOT.
There may be insufficient time to implement all steps in sequence. ERCOT can immediately implement Step 4 of the EECP any time the system frequency is below 59.8 Hz and will immediately implement Step 4 any time the frequency is below 59.5 Hz.
Percentages for Step 4 Load shedding will be based on the previous year's TDSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.
The ERCOT System Operator shall declare the EECP steps to be taken by QSEs and TDSPs. QSEs and TDSPs shall implement actions under that Step (and all above if not previously accomplished) and shall report back to the ERCOT System Operator when the requested step has been completed.

## Slide 34: Emergency Electric Curtailment Plan
To provide an orderly, predetermined procedure for curtailing demand during such emergencies, ERCOT has established this Emergency Electric Curtailment Plan.
The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

## Slide 35: Emergency Electric Curtailment Plan
There may be insufficient time to implement all steps in sequence. ERCOT CAN immediately implement Step 4 of the EECP any time the system frequency is below 59.8 Hz and WILL immediately implement Step 4 any time the frequency is below 59.5 Hz.
Percentages for Step 4 Load shedding will be based on the previous year's TDSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

## Slide 36: Step 1
Maintain ERCOT Undeployed Responsive Reserve Service Resources To 2300 Mw

## Slide 37
Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability.
Issue Dispatch Instructions to QSEs to suspend any ongoing generating unit or Resource performance testing.
Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive Reserves.
Utilize available DC tie capability that is not already being used by the market.
Notify the Southwest Power Pool Security Coordinator.
OOM uncommitted units available within the expected timeframe of the emergency.
Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

## Slide 38: Step 2
Maintain ERCOT Undeployed Responsive Reserve Equal To Largest Unit In Operation Or Greater

## Slide 39
In addition to measures associated with STEP 1
Instruct TDSPs to reduce customer loads by using distribution voltage reduction measures, if deemed beneficial by the TDSP.
Instruct QSEs to deploy winning bidders of Responsive Reserve, which is supplied from Load Acting As a Resource (controlled by high-set under-frequency relays), to remove such load.
With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer load from the ERCOT control area to Non-ERCOT control areas.

## Slide 40: Block Load Transfer

## Slide 41: EECP Step 2 CAA Procedure
Purpose:
Response to a frequency decay by using EECP Step 2 and the deployment of LAARs
Note:
UFR deployment is as follows:
Hydro RRS – 59.90 Hz
Sandow LAAR – 59.8 Hz
RRS LAARs – 59.7
NEW

## Slide 42: EECP Step 2 CAA Procedure
Condition:
Regulation Service is depleted AND frequency is below 60 Hz and continuing to decay.
ERCOT CAA Actions:
Attempt to deploy any remaining Balancing Energy.
OOME all RMR units on line to full load

## Slide 43: EECP Step 2 CAA Procedure
ERCOT CAA Actions: (cont.)
Issue a Fleet VDI to the 2 (two) QSEs showing the highest amount of spinning reserves available.
When issuing the VDI, the operator should request enough generation to restore frequency and recall approximately 50% of Regulation Up Service.

## Slide 44: EECP Step 2 CAA Procedure
2. If frequency continues to decay, ENSURE that 33% of Responsive Reserve supplied by generation resources is deployed
3. Verify that the Balancing Offset is set to an approximate value that will restore Regulation Service

## Slide 45: EECP Step 2 CAA Procedure
If Step 2 of this procedure does not arrest the frequency decay AND frequency reaches 59.85, IMPLEMENT EECP Step 2 and deploy all LAARs bid to supply Responsive Reserves.
Follow EECP Procedures as required.

## Slide 46: Step 3
3 Maintain System Frequency At 60 Hz

## Slide 47
In addition to measures under STEPS 1 & 2
Issue an appeal through public media for voluntary load reduction.
Confirm that all generators are at maximum generation and other Resources are being maximized.

## Slide 48: Step 4
Maintain System Frequency At 59.8 Hz Or Greater

## Slide 49
In addition to measures under STEPS 1 – 3.
Direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operating procedures in order to maintain a steady state system frequency of 59.8 Hz.
Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

## Slide 50: EECP Termination
ERCOT shall continue EECP until sufficient bids are received by ERCOT to eliminate the shortfall and restore adequate reserves.
Notes: ERCOT shall continue EECP until sufficient bids are received by ERCOT to eliminate the shortfall and restore adequate reserves.
OPERATORACTIONERCOTRestore full reserve requirements (normally 2300 MW)Terminate the steps in reverse order, where practical. Notify each QSE and TO of EECP Step termination.QSEs and TOsImplement actions to terminate previous actions as EECP steps are released in accordance with these guides.Notify represented Market Participants of EECP Step changes.Report back to the ERCOT System Operator when each Step is accomplished.Loads will be restored when specifically authorized by the ERCOT.
ERCOT shall maintain a stable ERCOT System frequency when restoring Load.

## Slide 51: Summary
The four emergency communications are
    Operating Condition Notice
    Advisory
    Alert
    Emergency Notification
The purpose of each emergency communication is:
    An Operating Condition Notice (OCN) will be issued by ERCOT to inform all QSEs of a possible future need for more Resources because of conditions that could affect reliability.

## Slide 52: Summary Continued
    An Advisory will be issued by ERCOT when it recognizes that conditions are developing or have changed such QSE or TDSP action is prudent in response to impending severe conditions.
    An Alert may be issued by ERCOT when it recognizes that conditions have developed such that an insecure operating state exists or is imminent.
    An Alert may also be issued by ERCOT when it recognizes that market Congestion Management techniques specified in these protocols will not be adequate to resolve transmission problems.

## Slide 53: Summary Continued
    ERCOT will only issue an Emergency Notice when it recognizes that immediate action is required.
The purpose of the four steps of EECP is:
  Step 1
    Maintain ERCOT Undeployed Responsive Reserve Service Resources To 2300 Mw
  Step 2
    Maintain ERCOT Undeployed Responsive Reserve Equal To Largest Unit In Operation Or Greater

## Slide 54: Summary Continued
  Step 3
    3 Maintain System Frequency At 60 Hz
  Step 4
    Maintain System Frequency At 59.8 Hz Or Greater
The basis for ERCOT transmission system reliability assessments is Single Contingency Criteria:

## Slide 55: Summary Continued
  Generation
      The Forced Outage of two generating units in the ERCOT System within a short period of time .
  Transmission
      The Forced Outage of any single transmission element (such as a circuit or transformer).
      The Forced Outage of a double-circuit transmission line (DCKT) will be considered a credible single contingency

## Slide 56: Reference Sources
ERCOT Protocols
ERCOT Operating Guides

## Slide 57: Exam
Which section of the ERCOT Operating Guides addresses emergency operations?
  Section 1
  Section 2
  Section 3
  Section 4

## Slide 58: Exam Continued
2. Which of the following is NOT an ERCOT emergency communication?
  OCN
  Market Bulletin
  Advisory
  Emergency Notification

## Slide 59: Exam Continued
3. During which emergency communication can ERCOT increase the Day-Ahead market to Two-Days-Ahead?
  OCN
  Advisory
  Alert
  Emergency Notification

## Slide 60: Exam Continued
4. Which emergency communication would ERCOT issue when an insecure operating state is imminent?
  OCN
  Advisory
  Alert
  Emergency Notification

## Slide 61
5. ERCOT can immediately implement Step 4 of the EECP any time the system frequency is below ____ Hz?
  59.9
  59.8
  59.7
  59.5
Exam Continued

## Slide 62: Exam Continued
6. The goal of EECP Step 1 is to maintain ERCOT undeployed Responsive Reserve Service resources to ____ Mw?
  1150
  2000
  2300
  2500

## Slide 63: Exam Continued
7. During EECP Step 2, TDSP’s may be instructed to _____?
  Shed load
  Implement Transformer Voltage Reduction
  Issue a public appeal for voluntary load reduction
  Implement Block Load Transfer
    a and b
    a and c
    c and d
    b and d

## Slide 64: Exam Continued
8. Percentages for Step 4 Load shedding will be based on the__________?
  Previous year's TDSP peak load
  Previous year’s REP peak load
  TDSP available firm load
  Deficit area’s available firm load

## Slide 65: Exam Continued
9. Transmission system security is assessed by _____?
  Facility ratings
  Transient voltage stability
  Frequency
  Single Contingency Criteria

## Slide 66: Exam Continued
10. ERCOT shall continue EECP until sufficient bids are received by ERCOT to ________ and __________?
  Eliminate the shortfall
  Restore adequate reserves
  Maintain 60 Hz
  Restore service to critical loads
    a and b
    b and c
    c and d
    a and c