| PRR Number | 590 | PRR Title | Update Unit Telemetry Requirement |
| --- | --- | --- | --- |
| Impact Analysis Date |  | April 6, 2005 |  |
| Credit Impacts |  | YES _______ NO ______ If No, skip the next two boxes. |  |
| Has the Credit Workgroup reviewed the PRR? |  | YES _______ NO ______ |  |
| Outcome of Credit Workgroup review |  |  |  |
| Cost/Budgetary Impact |  | 6-LL (Less than $100k) - The impact is the same as the impact for OGRR165 (same title). |  |
| Estimated Project Time Requirements* *Unless otherwise indicated, project time requirements begin upon project initiation. |  | ERCOT needs approximately three months to coordinate SCADA (Substation Control and Data Acquisition) changes and testing with QSEs representing Generation Resources. |  |
| ERCOT Staffing Impacts (across all areas) |  | Minor impact absorbed by current staff to complete testing. |  |
| ERCOT Computer System Impacts |  | SCADA points need to be added to the ERCOT EMMS system to receive the AGC status and ramp rate for each appropriate generating unit. Accompanying changes to ERCOT’s ICCP (Inter-Control Center Protocol), RTU (Remote Terminal Unit), and PI (Plant Interface) systems will also be necessary to complete the mapping of the SCADA points. |  |
| ERCOT Business Function Impacts |  | None anticipated. |  |
| Grid Operations & Practices Impacts |  | ERCOT will be able to monitor real-time AGC status and ramp rates of each appropriate generating unit. |  |

Alternatives for a More Efficient Implementation (include explanation of impacts)

N/A

Evaluation of Interim Solutions (e.g., manual workarounds)

N/A

Comments

This PRR is the result of Recommendation 14 by Potomac Economics. Implementation will provide ERCOT Operations visibility into real-time AGC status and ramp rates of each appropriate generating unit.