| PRR Number | 590 | PRR Title | Update Unit Telemetry Requirement |
| --- | --- | --- | --- |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |  |
| Requested Resolution (Normal or Urgent) |  | Normal |  |
| Revision Description |  | This revision proposes to add a requirement for QSEs to submit real-time AGC status and Ramp Rate for all online units in their portfolio. |  |
| Reason for Revision |  | ERCOT submits this PRR to address Recommendation No. 14 of Potomac Economics’ recommendations to improve ERCOT’s wholesale market design. Recommendation No. 14 states that ERCOT should monitor a QSE’s ability to meet its Responsive Reserve Obligation in real-time. Currently, capacity is monitored, but a unit’s ramp rate is not monitored. This revision will incorporate a unit’s ramp rate and Automatic Generation Control (AGC) status in the data provided to ERCOT. |  |
| Credit Implications (Yes or No, and summary of impact) |  |  |  |
| Timeline |  |  |  |
| Date Posted |  | 4/1/05 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Dumas |
| E-mail Address | jdumas@ercot.com |
| Company | ERCOT |
| Company Address | 7620 Metro Center Drive, Austin, TX |
| Phone Number | 512-248-3195 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | Not known | Add real-time SCADA points and archive to PI | Improves ERCOT’s ability to determine if QSEs could have met a Responsive Reserve Obligation within 10 minutes |
| MARKET SEGMENT | Not known | Not known | Not known |
| Consumer | Not known | Not known | Not known |
| LSE: General, Including NOIE | Not known | Not known | Not known |
| LSE: CR & REP | Not known | Not known | Ensures that purchased RRS is ready to be deployed in case of emergency |
| QSE | Not known | Possible creation of new SCADA points | Possibly allow for more effective dispatch of units |
| Resource | Not known | Not known | Not known |
| TDSP | Not known | Not known | Not known |

Proposed Protocol Language Revision

6.5.1.1	Requirement for Operating Period Data for System Reliability and Ancillary Service Provision

Operating Period data will be used by ERCOT to monitor the Real Time reliability of the ERCOT System, and will be used in network analysis software to predict the short-term reliability of the ERCOT System.  Each TDSP, at its own expense, may obtain such Operating Period data from ERCOT or from QSEs.

(1)	A QSE representing a Generation Entity that has Generation Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit at a Generation Resource plant location and ERCOT will make the data available to the Generation Resource’s host TDSP (at TDSP expense):

(a)	Gross or net real power;

(b)	Gross or net Reactive Power;

(c)	If gross quantities are provided, the plant auxiliary Load data will also be supplied;

(d)	Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System;

(e)	Frequency Bias of Portfolio Generation Resources under QSE operation;

(f)	Any data mutually agreed by ERCOT and the QSE to adequately manage system reliability;

(g)	Generator breaker status;

(h)	High Operating Limit;

(i)	Low Operating Limit;

(j)	AGC Status; and

(k)	Ramp Rate.

[PRR307: Revise Section 6.5.1.1(1) and 6.5.1.1(1) (c) & (g) as follows when system change implemented.] (1) A QSE representing a Generation Entity or a Competitive Retailer that has Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit or LaaR capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) at a Resource plant location and ERCOT will make the data available to the Resource’s host TDSP (at TDSP expense): (c) If gross quantities are provided, the plant auxiliary Load data will also be supplied as needed to determine the net output; (g) Resource breaker status;

(2)	Any QSE providing Responsive Reserve and/or Regulation must provide for communications equipment to receive ERCOT telemetered control deployments of service power.

(3)	Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Generation Resources.

(4)	Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using LaaR shall provide separate telemetry of the real power consumption of each LaaR providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that LaaR.  If LaaR is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

[PRR307: Revise Section 6.5.1.1(3) and 6.5.1.1(4) as follows when system change implemented.] (3) Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Resources. (4) Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using interruptible Load as a Resource shall provide separate telemetry of the real power consumption of each interruptible Load providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that interruptible Load. If interruptible Load is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

(5)	Any QSE that represents a qualified provider of Balancing Up Load (BUL) need not provide telemetry but rather shall provide an estimate in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load.

(6)	Real Time data for reliability purposes must be accurate to within three percent (3%).  This telemetry may be provided from relaying accuracy instrumentation transformers.