## Slide 1: Generation Adequacy Task Force Report to TAC
April 7, 2005

## Slide 2: Progress
GATF has met a total of five times since February.
Reached general consensus on all components of the ERCOT Reserve Margin Calculation Equation except:
  DC Ties and
  “Mothballed” Units.

## Slide 3: Current ERCOT Reserve Margin Calculation Methodology
Firm Load = Forecasted total summer peak demand – LaaRs – BULs
Available Resources = Installed Capacity (excluding wind generation)
+ 100% of DC Ties
+ 100% of “Switchable” Capacity
+ 10% of Wind Generation
+ 100% of Planned Generation (with signed Interconnect Agreement)
+ 10% of Planned Wind Generation (with signed Interconnection Agreement)
- 100% of “Mothballed” Units (first year of forecast only)
- 100% of Retiring Units (all forecast years)
Reserve Margin = (Available Resources – Firm Load)/Firm Load

## Slide 4: Disclaimer
The GATF recognizes that there is uncertainty associated with a number of the inputs to the ERCOT Reserve Margin Calculation (e.g., load forecast, market price impacts on capacity available from DC ties, “switchable” units and mothballed units, etc.). The following recommendations consider these uncertainties to the extent possible in a formulaic approach while attempting to produce an equation to calculate an ERCOT reserve margin forecast that produces a reasonable estimate of such reserve margins while not being overly cumbersome or complex. The GATF recognizes that it is not possible to create an equation that can capture all of the subtle and not-so-subtle impacts of market prices on capacity reserves. But the GATF believes that the following recommendations represent an improvement in the existing ERCOT reserve margin calculation.

## Slide 5: Consensus Items: Load
ERCOT econometric load forecast will be used for the next CDR calculation (likely to be in May 2005).
Amount of Load resources to include is based on recommended eligibility criteria from the Demand-Side Working Group (DSWG):
    Contractual with obligation to perform
    Dispatchable or controllable by ERCOT
    Load availability needs to coincide with system peak
    Need measurement and verification (M&V) for deployments (responsibility of host)
    Long-term (contract or installed control equipment investment)
    Subject to review by ERCOT
    Annual reporting of subscription

## Slide 6: Consensus Items: Load
GATF Recommendation:
Initially set load participation value at 1,150 MW, based on the amount of RRS that ERCOT currently deploys from LaaRs on a daily basis and 0 MW for load participation in nearly all other Ancillary Services (same as current methodology).
After 2005, base the amount of load participation on historical use in providing RRS:
  Load Participation (RRS) = Historical Self-Arranged + [(Historical Amount Bid into RRS market by LaaRs) x Z], but no greater than ERCOT established participation level (i.e., currently 1,150 MW), where Z is to be determined as additional historical summer data becomes available that the resources will be available during summer peak load periods. A method for determining the value of Z has not yet been established.
The historical actual average amounts for each year will be based on a rolling average of up to 3 years of historical data for weekday hours beginning 16:00-18:00 during the months of July and August for each year.

## Slide 7: Consensus Items: Load
After 2005, the same methodology will be applied to determine the contribution from Non-Spin, Replacement Reserve Services and Balancing Up Loads (BULs) to the extent that loads actually participate in any of these services.
Contributions from load management programs operated by other market participants that conform to the eligibility criteria will also be included (after submittal of verification data by host to ERCOT) unless they are implicitly included in ERCOT’s peak demand forecast (i.e., no double-counting).
A Protocol Revision Request (PRR) will be developed and submitted to establish reporting requirements for load management programs operated by other market participants that meet the eligibility criteria.

## Slide 8: Consensus Items: Installed Capacity
Currently use capacity as shown in resource registration, as updated through a questionnaire last fall.
GATF Recommendation:
  Use Net Summer Dependable Capability pursuant to ERCOT testing requirements.

## Slide 9: Consensus Items: New Installed Capacity
Currently include capacity that has a signed Generation Interconnect Agreement.
GATF Recommendation:
  No change but also include capacity from any NOIE that has submitted a letter to ERCOT regarding the interconnection of new generating capacity pursuant requirements contained in the ERCOT Power System Planning Charter and Processes.

## Slide 10: Consensus Items: Wind Generation
Currently use 10% of installed capacity
GATF Recommendation:
  Use actual historical hourly production data for weekday hours beginning 16:00 – 18:00 for the months of July and August;
  weighted by installed capacity;
  apply a confidence level for wind resource availability rate that is equal to one minus the capacity–weighted system equivalent forced outage rate used in the most recent LOLP study (8% FOR);
  use up to 10-years of actual data (currently, 3 years of data is available).

## Slide 11: Consensus Items: Wind Generation
ERCOT will update the calculation every year using actual data from the previous calendar year.
Based on current data available (years 2002-2004), the capacity value for wind generation will be 2.9% for all ERCOT CDR calculations prepared in 2005.

## Slide 12: Consensus Items: “Switchable” Units
Currently include 100% of capacity of “switchable” units
GATF Recommendation:
  For “switchable” units, use the Summer Net Dependable Capability of “switchable” units less the amount of capacity reported by the owners of “switchable” capacity to be unavailable to ERCOT during the summer peak load period as the result of a unit-specific contract for delivery outside of ERCOT.
A PRR will be prepared to require owners of “switchable” capacity to report the amount of “switchable” capacity unavailable to ERCOT as the result of a unit-specific contract for delivery outside of ERCOT.

## Slide 13: Non-Consensus Items: “Mothballed” Capacity
Currently assume that 100% of “mothballed” capacity is not available in the first year of the forecast and that 100% is available in the second through fifth years of the forecast.
Option 1 – Essentially creates a range for reserve margin depending on how “mothballed” units are counted. The upper end of the range assumes 100% of “mothballed” units are available in every year of the forecast subject to the lead-time required to return the unit to service as reported pursuant to PRR 573. The lower end of the range assumes that none of the “mothballed” units return to service during the forecast period. For reporting purposes, the upper end of the range will be used.
Option 2 – Use Probability Matrix which considers technology type, lead-time to return to service and length of time the unit is in mothballed state.

## Slide 14: “Mothballed Capacity” Probability Matrix
 | No. of Years Mothballed |  |  |  |  | 
Technology | 1 | 2 | 3 | 4 | 5 | 6
Steam Non-Reheat | 40% | 40% | 20% | 0% | 0% | 0%
Steam Reheat | 50% | 50% | 30% | 10% | 0% | 0%
CCCT | 75% | 75% | 55% | 35% | 15% | 0%
CT | 80% | 80% | 60% | 40% | 20% | 0%

## Slide 15: Non-Consensus Items: DC Ties
Currently, use 100% of ERCOT DC Tie import capability (856 MW)
Option 1 - Based on Southwest Power Pool (SPP) Capacity
  Calculate the amount of excess capacity available in the SPP by subtracting the SPP load and minimum reserve requirement from SPP’s capacity;
  multiply the result by 50%; and
  apply the lesser of: the 50% SPP excess capacity number as calculated above or the maximum ERCOT DC Tie import capability (currently 856 MW).
Option 2 - Use 50% of the maximum ERCOT DC Tie import capability (428 MW).