April Report

To

Technical Advisory Committee

Reliability and Operations Subcommittee

Prepared by ERCOT Transmission Services

Status of major transmission projects

Status of active generation interconnection requests

Studies completed or underway

- Middle Rio Grande Valley Project Review has been completed.  Acceptance letter has been completed.  ERCOT Review and AEP/MVEC report posted in operations and planning data area Regional Planning Group South data folder

- System Protection Working Group Support - 2005 Current Year short circuit base case has been built and posted in the operations and planning data area in the System Protection Short Circuit Data

- Zorn SPS was reactivated when the Hays Plant terminated its mothball status.  This SPS was recently disabled again because LCRA is installing a new autotransformer at the Kendall substation.  This SPS will be revised and resubmitted for approval when improvements are complete

- A revised Marion SPS submitted by LCRA completed the ERCOT SPS approval process and the letter of approval has been sent to LCRA

- Review of AEP Reactive Plan for the McCamey Area Completed – Plan is sufficient for 755 MW wind export

- Review of April 28 McCamey generation event discussed with Operations, TDSP and generator owner

- Texas Genco Suspension of Operations Completed

  - Identified a PH Robinson unit as RMR based on ERCOT Planning Criteria Voltage Stability Margin for the Houston area Report posted in operations and planning data area in RMR Studies data folder

- Continue support to Steady State WG to build base cases(Data Set A & B) with extensive case checking and review

- Continue support to Dynamics WG including 2005 flat start incorporating wind farm models

- Continue support to System Protection WG

- Continuing  to increase fidelity of planning base cases, operating cases and contingency files

- Continuing support to the Transient Voltage Dip analysis of the Corpus Christi area, work performed by Siemens/PTI in cooperation with Flint Hills and AEP TCC

- Continuing support of stability load modeling project (EPRI Solutions)

- Continuing support of Utility Wind Interest Group (UWIG) wind farm stability modeling effort

- New project for review in RPG process to place a new 345/138 kV autotransformer at Clear Springs, building a double breaker 138 kV station and upgrading two 138 kV lines

- Bryan and College Station Reliability Study underway

- DFW/NE Congestion 2006 Study is nearly complete as well as the NE-SPS removal study

- DFW/NE 2008/2009 Congestion Study (draft scope will be discussed at 5/11/ North RPG meeting)

- PH Robinson RMR exit strategy

- Killeen Reliability Study

- Lower Rio Grande Valley Reliability Study

- October 1 Report

- Annual Survey of Critical Voltage Stability Events (reliability/security protected information)

- Annual Survey of Critical Transient Stability Events (reliability/security protected information)

- Dynamic limit evaluation of 2005 CSC/CM zonal transfers

- 345/138 kV Autotransformer congestion and investigate possible planning criteria change

- Incorporate Planning Charter into Operating Guides

Upcoming Events

- North Regional Planning Group May 11 ACC (MET Center), 9:30 AM to 3:30 PM

- SSWG 2006 Data Set A base case creation

- NERC Planning Committee Transmission Issues Subcommittee meeting (PC TIS) 05/23-24/2005

- NERC Operating Committee Transmission Subcommittee meeting (OC TS) 06/15-16/2005

Other Issues

- Undervoltage Load Shed (UVLS) meeting was held April 1 at ACC (MET Center) with stakeholders reviewing current activities and NERC requirements.  Input into other locations addition for UVLS is due to ERCOT June 1.

- NERC PC TIS Multiregional Modeling Work Group needs to review their procedural manual to confirm it is compliant with NERC compliance efforts. ERCOT is tasked to review the SSWG procedural manual to make sure it is compliant with NERC standards

- Responding to NERC recommendations ROS Dynamics WG will simulate an actual event to test dynamic models

- Consistency of data between planning and operations needs to be improved. NDSWG and SSWG need to continue to fully support this ongoing effort

- Operations and Planning model synchronization efforts are ongoing and should be a high priority for each TO.  Much success has already been achieved, but there is still a lot of work to do

- Timing of AEP McCamey reactive plan is important, especially the dynamic reactive device at Crane and the McCamey capacitor banks

- Full interconnection studies done by TDSP’s did not include other active confidential projects even though electrically very close to the study project. TDSP’s need to coordinate on these efforts.

- TDSPs need to provide correct identification of the region in which projects are located  in Transmission Project Information Tracking (TPIT)

- Evaluating new projects using the SSWG base cases is difficult because they include projects major projects that have not been processed by the Regional Planning Groups.  The first step in any project evaluation study has to be to remove major transmission elements which may affect the project that have not been studied by the RPG – which increases the time required study the proposed project by several weeks.  This delay could be avoided if major transmission system project (ones that would be required to go through RPG review) were not be included in base cases unless they have gone through the RPG process.  It may still be appropriate to include planned projects that are not required to go through the RPG process, but this needs more consideration.  However, in order to keep the market informed about prospective projects that have not yet gone through review, these projects should be included in TPIT, with the appropriate modeling information and an appropriate indicator that the project is not included in the SSWG cases.

Interesting observations

- Review of 1 year of settlement data indicates one non-McCamey wind plant indicated that generation output exceeded 95% of installed capacity 0.8% of time.  Generation output exceeded 80% of installed capacity 17.6% of time

- Mothball/decommission of generation is reducing voltage stability margins

Future issues

- Ensuring base cases are built including accurate generator net dependable MW capability

- Developing/applying accurate generator reactive capability curves

- Development of Combined Cycle Stability Models postponed to 2006 due to budget reduction, will be included in 2006 budget submission

- Reviewing whether any changes made by Generation Adequacy Task Force (GATF) should change any transmission planning procedures

Internet Links

- Operations and System Planning Data area

  - http://www.ercot.com/tmaps/Login.cfm

  - Major data folders of interest in this area

    - Power System Planning Charter & Processes

    - October 1 Report to PUCT Annual

    - CSC CM Zone 2005 Data Files

    - Capacity, Demand, and Reserve Reports

      - Report on generation capacity, projected demand and reserves

    - Contingency Information – planning

    - Demand and Energy Reports (D&E) Monthly Actuals

      - Monthly actual demand and energy report

    - EIA-411 DOE Regional Electricity Supply and Demand Projections

    - Generation Project Interconnection Information

      - Public new and existing generation projects in ERCOT since 1996

    - Maps of ERCOT Transmission System

    - Operations Engineering Procedures

    - Operations Model Data

      - System Operations Base Case updated often

    - Regional Planning Group NORTH

    - Regional Planning Group SOUTH

    - Regional Planning Group WEST

    - Reliability Must-Run (RMR) Studies

    - Special Protection Schemes (SPS) Information

    - Steady State Base Case Info & Old Data

    - Steady State Power Flow Base Cases 2005 Data Set A (2005 eight seasonal cases)

    - Steady State Power Flow Base Cases 2005 Data Set B (2006-2010 cases)

    - System Protection Short Circuit Data

    - TNT Cost Benefit Study Data

    - Transmission Project & Information Tracking (TPIT)

    - Voltage Security Study of ERCOT System

    - Wind Stability Modeling ERCOT Project