## Slide 1: ERCOT Cascading outage Practice & Possible improvement
John Adams
ROS – May 12, 2005

## Slide 2: NERC Standard 0 definition of Cascading
The uncontrolled successive loss of sysem elements triggered by an incident at any location. Cascading results in widespread electric service interruption that cannot be restrained from sequentially spreading beyond an area predetermined by studies.

## Slide 3: Guides use of Cascading: 5.1.4 - Planning
The contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans), such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

## Slide 4: Guides use of Cascading 7.2.2 (14):
The owner(s) of existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database. The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.
ERCOT shall conduct a review of proposed or modified SPS before the SPS is placed in service. This review shall verify that the SPS complies with ERCOT and NERC criteria and guides. The review shall include system studies verifying that failure of a single component of the SPS, which would result in failure of the SPS to operate when required, would not result in cascading transmission outages. The review shall also verify that misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, shall meet the system performance requirements of all applicable NERC criteria. This review shall be documented and the documentation provided to NERC on request within 30 days.

## Slide 5: Protocols Use of Cascading 5.6.6:
Emergency Notice
ERCOT will issue an Emergency Notice only for the following reasons:
ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market;
ERCOT is in an unreliable condition, as defined below;
Immediate action must be taken to avoid or relieve an overloaded transmission element; or
ERCOT varies from timing requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures.
The actions ERCOT takes during an Emergency Condition will depend on the nature and severity of the situation.
ERCOT is considered to be in an unreliable condition whenever ERCOT Transmission Grid status is such that the most severe single-contingency event presents the threat of uncontrolled separation or cascading outages and/or large-scale service disruption to Load (other than Load being served from radial transmission service) and/or overload of a critical transmission element, and no timely solution is obtainable from the market.

## Slide 6: Guides use of Cascading 4.2.4:
ERCOT is considered to be in an insecure state whenever ERCOT Transmission Grid status is such that the most severe single-contingency even presents the threat of uncontrolled separation of cascading outages and/or large-scale service disruption to Load (other than Load being served from a single-feed transmission service) and/or overload of a critical transmission element, and no timely solution is obtainable from the market.
ERCOT will only issue an Emergency Notice when it recognizes that immediate action is required because:
ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market
ERCOT must avoid or relieve an overloaded transmission element
ERCOT is in an insecure state
ERCOT varies from Timing Requirements or omits one or more Scheduling Procedures

## Slide 7: Current Practice
When a Transmission Element is loaded post contingency; either single transmission element or double transmission element above its emergency rating; it is assumed to be a potentially cascading event.
This action is required by NERC standard TOP-004-0 which states: “If a transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes.

## Slide 8: ERCOT Current Processes cont.
Currently there are about 2100 contingencies defined in the ERCOT Network Analysis database (CTGS) Posted on ERCOT website.
162 of them are double-circuit contingencies, roughly 8% of total contingencies defined
1348 double circuit/single tower contingencies over .5 mile exist. (ERCOT Operations models ~12% of those existing)
In general, ERCOT models all known 345 kV double circuit contingencies, and select 138 kV double circuit contingencies.

## Slide 9: ERCOT Protocols
ERCOT and TDSPs shall operate the ERCOT system in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures. (5.2.2)
ERCOT Dispatch Instructions shall respect all equipment operating limits. (5.2.3)

## Slide 10: ERCOT Operating Guide 2.2.2 Security Criteria - continued
A credible single contingency is defined as the Forced Outage of two generating units in the ERCOT system within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer). The Forced Outage of a double-circuit transmission line will be considered a credible single circuit contingency during any ERCOT declared Alert or for any operating condition characterized by high DCKT Outage probability or consequence.

## Slide 11: ERCOT Operating Guide 4.3 Operation to Maintain Transmission..
“Single contingency” criteria are specified as follows:
A credible single contingency is defined as the Forced Outage of two generating units in the ERCOT System within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer).
The Forced Outage of a double-circuit transmission line (DCKT) will be considered a credible single contingency for any of the following operating conditions characterized by high DCKT Outage probability or consequence:
High Outage Probability
Severe weather conditions are forecasted by ERCOT in the vicinity of the DCKT.
Weather conditions indicate a high risk of insulator flashover on the DCKT.
Individual circuits that are part of the DCKT have experienced repeated Forced Outages within the preceding 48 hours possibly indicating unresolved problems.
A high risk of DCKT Outage exists due to fire in progress near the DCKT right-of-way.
High Outage Consequence
Another transmission Facility, which significantly increases the impact of an Outage to the DCKT, is out of service.
Studies indicate Outage of the DCKT would result in cascading outages or voltage collapse.
Studies indicate Outage of the DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures in time to prevent equipment damage or failure.

## Slide 12: ERCOT guide 3.1.6
In operating the Transmission Grid ERCOT shall use these ratings as follows:
  ERCOT shall limit pre-contingency flows to enforce the Continuous Rating
  If a valid Remedial Action Plan is unavailable to unload the Transmission Facility post contingency …ERCOT shall enforce pre-contingency system Operating Limits(s) to control the post contingency loading of the facility to levels below the Emergency Rating…
  If a valid Remedial Action Plan is documented at ERCOT to relieve the loading on the Transmission facility within fifteen minutes; ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Fifteen Minute Rating.

## Slide 13: Then vs Now
In the late 90’s, when the wholesale market was in operation, the ATC calculation used multiple contingency lists which were implemented based upon weather in the area. At that time TDSPs/control areas had control of generation and transmission and could relieve reliability violations independently from ERCOT.
Today there is no reliability organization outside of the ERCOT Control Area to maintain ERCOT reliability. Many operating changes have reduced the operating reliability margin since the 1990’s
  Dynamic Ratings – reduced margin
  RAP’s; SPS – reduced margin
  Daily stability analysis instead of annual – reduced margin
  ERCOT intends to implement conditional RAP’s as soon as software is implemented
Historically the Control Area was the equipment owner, and could choose to risk its equipment. ERCOT, as an operator, not an owner, cannot accept a risk of rating violations outside of guide requirements.

## Slide 14: Conclusion
ERCOT position is that a line projected to be over its applicable rating post-contingency is a high consequence.
ERCOT is obligated to honor double circuit contingencies if it has a high consequence. (4.3)
ERCOT is obligated to prevent significant risk of… equipment overloads which cannot be eliminated through execution of specific pre-defined operating procedures in time to prevent equipment damage. ERCOT cannot recognize this high consequence of a double circuit outage without analyzing this outage. Section 3.1.6 obligates ERCOT to limit pre-contingency loading to avoid violating a post-contingency emergency rating. NERC TOP-004 obligates ERCOT to remain in a known secure operating condition.
Notes: NERC Version 0 tells us if you do not know the consequence of a forced outage you must treat a violation as an IROL.

## Slide 15: One Idea to reduce costs while maintaining security
Use DC power flow to evaluate how many buses will be shed assuming next line trips whenever above emergency limit.
Evaluate each double circuit outage using this software, and enforce congestion management if, and only if, expected load trip is > x MW.
If desired: Estimate risk = probability*load loss*Cost/mw. Set a threshold for allowable risk.
In parallel with this process, execute Voltage Stability Analysis (VSAT) and Transient Stability Analysis (TSAT) on double circuit contingencies and constrain as neeeded.

## Slide 16: another Idea to reduce costs while maintaining security
Use power flow to evaluate if opening overloaded line relives all security violations. If so, take no congestion management action.